U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

#### FISH FACILITIES WEEKLY REPORT

#14-2010

# Project:  McNary

# Biologists:  Brad Eby and Bobby Johnson

Dates:  May 28 – June 3, 2010

## Turbine Operation

McNary had 12 to 13 units available for power generation this week.  Unit 9 remains out of service for an asbestos removal.  On June 3, unit 8 returned to service after removal of asbestos.  The hard constraint, one percent criterion continues at the same time with the one percent criteria study on units 4 and 5.  This alternates everyday Monday through Friday.  The switch begins at noon each day with one unit outside the criteria at approximately 70 megawatts and the with the other unit running at the upper limit of the criterion.  The units are returned to their normal load ranges at approximately 2200 hours each night.  On May 31, the two units ran at normal loads as the researcher did not work the holiday.  No other units ran out side the criterion this week.

## Adult Fish Passage Facilities

On May 29, 31 and June 2, the McNary fisheries biologist performed measured inspections of the adult fishways.  Adult fish counting season continues.

### Fish Ladders:  During measured inspections, all Fish Passage Plan criteria were met on both ladders except on May 31 when the Washington ladder’s head over weir measured 1.4 feet due to a regulating weir issue which was later resolved.  On the Oregon ladder, exit weirs 339 and 340 alarmed and were reset once.  On May 28, the Oregon exit’s north traveling screen alarmed and was found to be jammed.  The screen was removed for service.  During the week, the problem was examined and could not be resolved.  Further examination of the screen will be delayed a week or two as the exit’s crane which installs the screen’s bulkheads is receiving maintenance.  The south traveling screen has been operating well and differential monitoring has revealed no problems.  With the amount of floating debris in the river, both ladders’ picketed leads are being monitored daily.

Fishway Entrances and Collection Channel:  On both ladders, all inspection points were in criteria except on May 31 when south powerhouse entrance weirs SFEW1 and SFEW2 measured 8.8 feet.  Hydraulic gradients produced by the spill program continue to have some effect.  The collection channel velocity average 1.7 feet per second.

Auxiliary Water Supply System:  For the week, all three fish pumps ran with blade angles of 22 to 24 degrees with no interruptions reported.  The juvenile facility supplied the usual 450 cfs to the north powerhouse pool with no interruptions.  The Wasco County PUD unit also had no interruptions.

#### Juvenile Fish Passage Facility

The alternating spring season of primary and secondary bypass continues with the switch between the bypass modes occurring each morning at approximately 0700 hours.  Only two diversions from this scheduled occurred this week.  On May 31 and June 2, secondary bypass for an extra sample for the orifice light study occurred from 1800 to 2210 and from 1800 to 2355, respectively.  On May 31, only the B sample gate was in use at 20 percent.  On June 2, both gates were in use at five percent until the last hour when 15 percent was used to insure enough fish were collected for tagging.  For the report week, 575,595 smolts were bypassed.  The extra samples collected 4,043 fish for possible tagging.

Forebay Debris/Gate well Debris/Oil:  Forebay debris was light as flows and wind continue to disperse incoming floating debris.  Trash rack differentials have revealed no problems.  On June 2, the racks at unit 9 were cleaned with only a trace of debris being removed.  More cleaning will occur as project operations allow.  No problems were observed in the gatewell slots this week.

ESBSs/VBSs:  ESBS’s are installed at all units.  The screens at 5C, 6A and 9C slots remain in transducer bypass mode.  No ESBS camera inspections occurred due to the short work week.  VBS monitoring revealed one screen out of criteria at 4A slot when the unit was at 70 megawatts.  On June 2 and 3, this screen and three others were cleaned.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  For the week, 42 orifices were in use with no problems to report.  All systems operated well in automatic mode this week.  The fisheries staff continued monitoring the channel on all shifts during primary bypass days, VBS and trash rack cleaning along with observing all three orifice traps as time allowed.

Transportation Facility:  Spring bypass season continues with alternating days of primary and secondary bypass where all fish are returned to the river.  PIT tag detection will occur in the full flow pipe during primary bypass and throughout the facility during secondary bypass.  Smolt monitoring will only occur on secondary bypass days.  The primary (A and B) PIT tag slide gates remained turned off and closed as the return to river lines provide a better bypass route for PIT tagged fish.  The secondary (C and D) PIT/bypass gates were off and open as there are no studies requiring them this year.  The sample gates were functioned well and they were turned off or on at 0700 hours each day so they will function only during secondary bypass including the extra sampling days for the NMFS light study.  When the extra samples occur, COE data only includes adult fallback counts for that day.  This week, ice block checks of the return to river lines revealed no problems.  Arrangements are being made to return the repaired upstream barge mooring bit to the dock before transport season begins.

Transport Summary:  There is nothing to report.

River Conditions

River conditions during the week are outlined in Table 1 as provide by the smolt monitoring staff whose data day runs from 0700 to 0700 each day.  The spring spill program continued with 40 percent of project’s discharge scheduled to be spilled.  However, on June 3, spill in excess of powerhouse capacity began which was greater than 40 percent.  This is not reflected in the data due to the timing of the data day.  Next week’s report will contain this information.  As flows increase, spill changes for navigation lock usage have decreased.

Table 1.  River conditions at McNary Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF) |  | Water Clarity* (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 253.8 | 185.7 | 102.0 | 74.5 | 55.9 | 54.4 | 6.0 | 6.0 |

*Control room data.

Other

Inline Cooling Water Strainers:  The cooling water strainers were examined on May 24 and 26.  A total of 61 lamprey (60 mortalities, 1 live) were recovered along with 34 smolt mortalities.  The next cooling water strainer examination will occur in late June.

Invasive Species:  No invasive species were found during the May 1 detector inspection.  The next inspection is approximately scheduled for June 1.

Predatory bird counts continue with tailwater observations and forebay counts done twice and once daily, respectively.  The tailwater area had high counts of approximately 475 gulls, 16 pelicans and 17 cormorants.  At week’s end, 60 terns, which were first seen this week, were also counted.  Most birds were seen in the spill area with the highest counts occurring on swing shift when no hazing personnel are on duty.  At the bypasses’ out falls, the high counts were 25 gulls, eight pelicans and 13 terns, again with swing shift having the highest numbers.  Birds are working the outfalls early and late when hazing personnel are not present.  The water cannon operated well with APHIS personnel on duty seven days a week on day shift.  The forebay area had high counts of approximately 125 grebes and four pelicans with an occasional gull, cormorant and osprey seen.  No terns were noted in the forebay area.  One grebe entered the gatewell slots this week joining the two from last week for a total of three.  Two grebes passed to the collection channel leaving one grebe in the gatewell slots.  The two grebes in the channel passed out of the system with one being removed from the separator.

On May 31 and June 2, the zebra mussel station checks revealed no problems.

The orifice light, one percent criteria and adult lamprey passage studies continue along with GBT monitoring.

Project:  Ice Harbor

# Biologist:  Mark F. Plummer

Dates: May 28 – June 3, 2010

## Turbine Operation

All turbine units (1 - 6) were available for operation this reporting period.

## Adult Fish Passage Facilities

### Fish facility personnel inspected the adult fishways May 28, June 1, June 2, and June 3.

### Fish Ladders:  All north and south fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria

### Fishway Entrances and Collection Channel (inspection date order):  The south shore entrance (SFE) was off sill with a depth of 9.6 feet, off sill with a depth of 9.7 feet, off sill with a depth of 9.7 feet, and off sill with a depth of 7.8 feet.  The north powerhouse entrance (NFE) was off sill with a depth of 8.6 feet, off sill with a depth of 9.4 feet, off sill with a depth of 9.5 feet, and off sill with 9.5 feet. The north shore entrance (NSE) was off sill with a depth of 8.0 feet, off sill with a depth of 8.8 feet, off sill with a depth of 8.3 feet, and off sill with a depth of 9.6 feet.  Fishway entrance criterion is 8 feet depth, greater than 8 feet depth, or on sill.  All channel/tailwater differentials were in criteria, except June 3.  On this inspection, the SFE was at 0.7 feet.  The operator was notified to make adjustments to correct the differential.  Spill continues to make visual staff gage reading difficult due to rapid changes in water elevation at the staff gages.  Visual staff gage readings are reported in this report.

### Auxiliary Water Supply System:  2 of the 3 north shore fish pumps were operated without problems.  All north shore fish pump are in service.   6 of 8 south fish pumps were operated.  All 8 south fish pumps are in service.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  No problems to report.  Fish ladder exits are clear of debris and the bubblers are operating.

STSs/VBSs:  The STSs operation is in continuous operational mode.  The change to continuous mode was made due to the average fork length of sub-yearling Chinook or sockeye is less than 120 mm at Lower Monumental Fish Facility.  No problems were found during the May STS/VBS inspections.  June STS/VBS inspections are scheduled for the 15th and 16th.

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe:   The juvenile fish bypass is in operation.  20 orifices are open.

Juvenile Bypass Facility:  The bypass was put in operation March 8.

Juvenile Fish Sampling:  Sampling for fish condition Monday and Thursday.

Removable Spillway Weir:  The RSW is in operation.

Fish Sampling:  No fish sampling occurred Monday May 31 due to Memorial Day Holiday.

June 3:

| Species | Sampled | #Descaled | Morts | Avian Marks |
| --- | --- | --- | --- | --- |
| C-CH | 12 | 0 | 0 | 0 |
| UC-CH | 21 | 2 | 0 | 0 |
| C-CH-O | 1 | 0 | 0 | 0 |
| UC-CH-O | 9 | 0 | 0 | 0 |
| C-SH | 67 | 2 | 0 | 2 |
| UC-SH | 29 | 2 | 0 | 3 |
| C-COHO | --- | --- | --- | --- |
| UC-COHO | 1 | 0 | 0 | 0 |
| C-SOCK | --- | --- | --- | --- |
| UC-SOCK | 1 | 0 | 0 | 0 |
| TOTAL | 141 | 6 | 0 | 5 |

River Conditions

River conditions during the week are outlined in Table 1.  Spill for fish passage began April 3.

Table 1.  River conditions at Ice Harbor Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 124.3 | 71.4 | 55.2 | 26.8 | 55 | 55 | 4.8 | 4.8 |

*Unit 1 scrollcase temperature.

Other

Inline Cooling Water Strainers:  Cooling water strainers were last checked on May 12.

Invasive Species: No zebra mussels were observed when the inspection was performed June 1 and 2.

# Project:  Lower Monumental Dam

# Biologist(s):  William Spurgeon and Elizabeth Lindsey

Dates:  May 28 – June 3, 2010

## Turbine Operation

Turbine units are being operated within the hard constraint 1% operational criteria.  There were no turbine unit outages during this week.

Adult Fish Passage Facility

The adult fishway was inspected by Corps or State biologists on May 28, 29, 30, and June 2.

Fish Ladders: Fishway exit head differential and depth over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively) on all inspections.  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively) on all inspections.

### Fishway Entrances and Collection Channel: NPE 1 and NPE 2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections.  North shore channel/tailwater head was in criteria (1’-2’) on all inspections.

SPE 1 and SPE 2 weir gates were in sill criteria (criteria: > 8’ or on sill) on all inspections.  While on sill, the gate depth readings were 7.3’, 6.8’, 7.4’ and 7.3 feet.  South powerhouse channel/tailwater head was in criteria (1’-2’) this week.

SSE1 weir gate was in depth criteria or sill criteria (criteria: > 8’ or on sill) on all inspections.  While on sill, the gate depth readings were 7.8’, 7.3’, and 7.8 feet.  SSE2 was in criteria (6’ above sill) on all inspections.  South shore channel/tailwater head was in criteria (1’-2’) this week.

### Auxiliary Water Supply System: AWS pump 3 has been out of service to replace the bearing housing and repair the diffuser assembly.  This work is scheduled to be completed in 2010.  Pumps 1 and 2 were in service throughout this period.   Pump 3 is bulkheaded off to minimize water loss during two-pump operation.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 1.3 square yard of forebay debris observed during this period.  Gatewell debris ranged from 0-15% surface coverage.  No oil was observed in gatewells.

STSs/VBSs:  STS operation changed to continuous run on June 1 as average fork length of sub-yearling chinook was reported as less than 120mm.  STS inspections were conducted May 24 and 25 with all screens found in good operating condition.

Orifices, Collection Channel, Dewatering Structure, Flume:  The collection channel is operating with 19 orifices open.

Collection Facility:  Fish are being collected for transport.  The barge dock is showing evidence of rapid settling.  District Engineering is being contacted.

Transport Summary:  Every other day barging began on May 28 with no barge on the 29th.

River Conditions

River conditions during the week are outlined in Table 1.  Spring spill operation was initiated at 0001 hours on April 3.

Table 1.  River conditions at Lower Monumental Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF)* |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 123.8 | 70.3 | 31.3 | 25.9 | 54.0 | 52.5 | 3.9 | 3.6 |

*Scrollcase temperatures.

#### Other

Inline Cooling Water Strainers:  Cooling water strainers were last cleaned on May 12.  Fish recovered included 31 lamprey mortalities.

Invasive Species:  There were no zebra mussels observed at the monitoring stations on the May 7 inspection.

Project:  Little Goose

# Biologist:  Richard Weis

# Dates:  May 28- June 3, 2010

## Turbine Operation

All turbine units were available for service this reporting period except unit # 4.  Unit 4 was placed out of service on June 1 for an oil leak.  Unit # 4 was returned to service June 2 after repairs.  All turbine units were operated within 1% of best efficiency.

## Adult Fish Passage Facility

USACE and ODFW fisheries biologists performed measured inspections of the adult fishway May 28, 31 and June 3.

Fish Ladder:  The ladder exit head differentials ranged between 0 and 0.1 feet (criteria < 0.5 ft.).  Water depths over the weirs was 1.1 feet (criteria 1.0-1.3 ft.) for all three inspections and picketed lead head differentials held steady a 0.0 feet (criteria < 0.3 ft.).

Fishway Entrances and Collection Channel:  Channel to tailwater head differentials at fish entrances ranged between 1.06 and 1.74 (criteria 1.0 to 2.0 ft.).  SSE weir depths ranged between 8.34 and 8.84 feet (criteria ≥8.0 ft), NPE1 and 2 weirs rested on sill position and depths ranged between 5.46 and 7.24 (criteria ≥7.0 ft. or on sill).  NSE1 is manually positioned at 529.1 and depths measured between 8.62 and 10.2 feet (criteria ≥ 6.0 ft.).  NSE2 weir depth ranged between 6.10 and 6.18 feet (criteria ≥ 6.0 ft.).

Collection channel surface water velocities (criteria 1.5 to 4.0 fps) ranged between 1.6 and 2.0 fps near the SSE and 2.3 and 2.7 fps near the NSE.   Subsurface water velocities near the SSE (flowmeter) ranged between 0.7 and 1.4 fps.

Auxiliary Water Supply System:  All fish pumps operated within criteria during this report period.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Forebay debris remained light during this report period.  Gatewells remain clear of debris.

Spillway Weir:  The weir was operated in the high crest position (622 ft.) spilling approximately 7200 cfs.

ESBS/VBS:   All operating ESBS were within criteria this report period.    Drawdown measurements across trash racks, ESBS and VBS associated with turbine units 1, 2, 3, 4, and 5 were performed on June 3, all criteria were met.

Orifices, Collection Channel, Dewatering Structure, Flume:  The juvenile collection channel is operating with 23 open orifices.

Transportation Facility:  Collection and transport continued this report period.  Daily collection for the period ranged between 9,725 and 31,680 for a total of 136,221.  All fish were transported except for mortalities.  Descaling and mortality rates for this report period are 0.1% and < 0.1% respectively.

Transport Summary:  All barge transport operations were successfully performed.  Alternated day barging operations began May 30.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Little Goose Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 122.5 | 70.0 | 35.4 | 20.9 | 56.2 | 52.4 | 5.3 | 4.0 |

*Ladder temperature.

Other

Inlin Cooling Water Strainers:  Cooling water strainers were not inspected this report period.

Invasive Species:  The Zebra Mussel substrate monitor was inspected on May 26, no mussels were observed.  The next inspection for zebra mussels is scheduled for June 30.

Avian Activity:  USDA – APHIS performed piscivorous bird hazing.  Up to 25 gulls and 21 Cormorants were observed during a given day this report period.

Project:  Lower Granite

# Biologists:  Mike Halter and Ches Brooks

# Dates:  May 28 – June 3, 2010

## Turbine Operation

Lower Granite had turbine units 1, 2, 4, 5, and 6 available for power generation at the beginning of the report week.   Turbine unit 2 was out of service from 0700 hours to 1055 hours on June 2 for a planned outage to troubleshoot regulator problems.  Turbine unit 3 remained out of service for a rewind and will not be available until approximately December 31, 2010.

## Adult Fish Passage Facility

On May 28, 30, 31, and June 3 the Lower Granite fisheries biologists performed measured inspections of the adult fishway system.

Fish Ladder:  All criteria were met with the exception of the ladder weir depth at diffuser 14 which was 0.9 feet (0.1 feet below criteria) on the May 26 inspection (criterion 1.0 – 1.3 feet).

Fishway Entrances and Collection Channel:   Head differential readings remained within criteria at all adult fishway entrances during the weekly inspections.  Weir depths at the south shore fishway entrances were also within criteria on all inspections.  North powerhouse fishway entrance weirs were on sill all week due to tailwater elevations below 636.0 feet.  Weir depths at the north powerhouse entrances ranged from 5.7 to 7.8 feet.  Weir depths at the north shore fishway entrances were out of critieria all week with readings of between 4.9 and 5.3 feet (criterion ≥ 7.0 feet).  Weir depth readings at the north shore entrances are being sacrificed in order to maintain the requisite 1.0 foot of head differential.  Weekly velocity readings in the adult fishway collection channel transition pool area ranged from 0.87 to 1.02 feet per second and averaged 0.93 feet per second.

### Auxiliary Water Supply System:  Fish pumps 2 and 3 were operated during the week without any problems.

#### Juvenile Fish Passage Facility

The sample rate was decreased from 2% down to 1% at 0700 hours on June 3.  High river flows caused a significant increase in fish numbers late in the report week.

Forebay Debris/Gatewell Debris/Oil:  Debris accumulation in the forebay and gatewells was minimal during the week.   It was not necessary to hand-dip debris from any gatewells this week.

ESBSs/VBSs:   The last ESBS/VBS inspections were conducted on May 23.  The next inspections are scheduled for late June.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  There were no problems with any of these structures during the week.  Orifices are being backflushed every three hours around the clock to ensure they remain free of materials that might impact fish passage.  Higher flows toward the end of the week increased the amount of debris moving through the system.

Transportation Facility:   All operations have been going smoothly.

Transport Summary:  Every other day fish barging operations began on May 28. (May 29 was the first day without a fish barge.)  Fish are being barged from Lower Granite on the odd-numbered days of June.

Removable Spillway Weir:   Nothing to report on the RSW.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Granite Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 128.6 | 71.5 | 41.4 | 20.6 | 56.4 | 54.7 | 5.0 | 3.8 |

*Cooling line intake temperature.

Other

Inline Cooling Water Strainers:  Inspection of the inline cooling water strainers took place on May 26.   Another inspection is scheduled for mid to late June.

Invasive Species:   The zebra mussel trap at the adult fishway exit was last examined for zebra mussels on the May 17 inspection.  No evidence of zebra mussels was found.

Research:  The University of Idaho continued steelhead kelt research work at the recently constructed holding tanks upstream of the main fish facility.   Steelhead kelts are being examined to determine the changes that occur during sexual maturity and to determine post spawning changes associated with successful downstream migration and recovery to spawn again.  Dependent on the group, steelhead kelts were blood sampled, PIT-tagged, acoustic-tagged, trucked, barged, or returned back to the river during the report week.   Steelhead kelts were barged from Lower Granite on June 3.

NOAA-Fisheries personnel tagged fish for the survival study and transport study at the JFF trailers during the week.  This work is scheduled to end on June 11.

Idaho Department of Fish and Game personnel conducted genetic stock identification work on chinook and steelhead smolts from the lab during the week.  The goal of the study is to enumerate and characterize the natural production of spring/summer chinook salmon and steelhead above Lower Granite with regard to age composition and genetic stock identification.  Sampling is taking place every day with a goal of collecting between 2500 and 4000 genetic samples from both chinook and steelhead.

The adult fish trap continued operation at a 4% sample rate during the week.  Wild steelhead are being PIT-tagged and genetic and scale samples are being taken.  In addition, scale samples are being taken from one out of every 25 hatchery steelhead .  One out of every seven hatchery chinook are also being PIT-tagged and scale samples and genetic materials are being taken.  The Lemhi study regarding tagging 15 Lemhi-origin chinook has been completed