U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

#### FISH FACILITIES WEEKLY REPORT

#29-2010

# Project:  McNary

# Biologists: Brad Eby and Bobby Johnson

Dates:  September 10 - 16, 2010

## Turbine Operation

McNary had eight to nine turbine units available for power generation this week.  Turbine units 2 and 7 remain out of service for rewind.  Turbine unit 1 remains out of service in support of T1 transformer replacement which will take approximately six weeks.  Turbine unit 13 remains out of service for maintenance.  Turbine unit 14 returned to service September 14 following completion of the T7 transformer work.  Turbine units 11 and 12 were removed from service on September 14 in support of T6 transformer maintenance and leak repair.  Work on the T6 transformer should be completed next week.  On September 12, turbine units 10, 11 and 12 were out of service for a total of one hour in support of ESBS camera inspections.  No turbine units operated outside the 1% criteria this week.

## Adult Fish Passage Facilities

On September 10, 12 and 15, the McNary fisheries biologist performed measured inspections of the adult fishways.  Adult fish counts continued.  Oregon entrance weirs SFEW1, SFEW2 and NFEW1 are being lowered on scheduled nights as part of the adult lamprey passage study.  No problems have been observed.  Temperature monitoring of the fishway exits concluded September 16.

Fish Ladders:  Both ladders met all Fish Passage Plan criteria during measured inspections.  At the Oregon exit, the regulating weir along with tilting weirs 337 and 340 occasionally triggered alarms.  In each case, normal operation resumed after alarms were reset.  The north traveling screen at the Oregon exit remains out of service.  The south Oregon exit traveling screen operation and differential monitoring results have been satisfactory even though differential alarms sound at times.  Regulating and tilting weirs at the Washington ladder exit were examined and adjusted by the technical staff this week.  The picketed leads hoist near the Washington exit also underwent electrical maintenance this week.  Both ladder exits are being monitored daily.

Fishway Entrances and Collection Channel:  All Washington ladder inspection points were in criteria this week as were most Oregon ladder inspection points.  Oregon fishway inpections points not meeting criteria included the north powerhouse pool differential (measured 0.5 to 0.7 feet all through the week), SFEW2 on September 12 (8.8 feet), and the south pool differential on September 15 (0.5 feet).  In addition, SFEW1 and SFEW2 respectively measured depths of 8.9 and 8.6 feet on September 15 due to fish pump 2 being out of service at the time of the inspection.  Collection channel velocities averaged 1.2 feet per second.

### Auxiliary Water Supply System:  For the week, fish pumps 1 and 2 ran with blade angles of 30 degrees.  Only pumps 1 and 2 are being operated due to the T1 transformer outage.  Operation of all 3 fish pumps requires both transformers T1 and T2 being available for service. On September 15 from 1250 to 1319 hours, fish pump 2 was taken out of service in support of cover plate flood pump repairs.  Flood pumps remove excess water from the individual sumps associated each fish pump.  Otherwise, both available fish pumps operated satisfactory this week.  The juvenile facility supplied the usual 450 cfs to the north powerhouse pool with no interruptions in service.  The Wasco County PUD turbine unit had two interruptions in service this week in support of T7 transformer work.  This maintenance took place on September 13 from 1744 to 1818 hours and on September 14 from 0639 to 0831 hours.  The bypass system worked well during both of these outages.

#### Juvenile Fish Passage Facility

Collection for truck transport continued as did daily trucking operations to insure that no smolts would be bypassed due to the numbers of shad present.  For the report week, 8,725 smolts, 60 juvenile lamprey, and 98,725 juvenile shad were collected.

Forebay Debris/Gate well Debris/Oil:  Forebay debris was very light and consisted of mostly Eurasian milfoil and minor amounts of bark chips.  Trash rack differentials were satisfactory and no raking took place this week.  Slots 1B, 1C, 2A, 2B, 13B and 14A remained covered in support of transformer T2 and T7 replacements.  Slots 12A and 3B were also covered on September 14 and 15 (respectively) in support of this transformer work.  No other problems were observed this week.

ESBSs/VBSs: ESBSs are currently deployed in all turbine units.  The screens in slots 5C, 6A, 9C and 10C slots remain in transducer bypass mode.  On September 12, the screen in 5A slot was noted to have a lower cycle count than the screens in slots 5B and 5C.  Although no reason was found for this discrepancy, the cycle counts for all three screens were reset.  On September 16, facility personnel noted that the PLC (programmable logic circuit) display for the screen in slot 5A was not being shown in feet even though brush travel was evident.  The mechanism appeared to be functioning despite the discrepancy.  The technical staff has been asked to examine the screen along with the PLC.  This screen is now scheduled for video-camera inspection on September 19.  Camera inspections were conducted in turbine units 10, 11 and 12 on September 12.  All inspected screens were found in satisfactory condition.  VBS differential monitoring efforts revealed two screens out of criteria.  These screens and six others were cleaned on September 14, 15 and 16 with the screen in slot 3A being cleaned twice.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  For the week, 39 orifices were in use as forebay elevations were stable.  An orifice associated with turbine unit 2 (currently out of service) continues to be opened or closed as required.  Reduced orifice count during high forebay elevations allows more efficient operation of the side dewatering valves.  All systems operated well in automatic mode.  Finally, the channel was monitored during VBS cleaning.

Transportation Facility: Truck transport took place daily this week.  Primary (A and B) PIT tag slide gates are currently in service and PIT tagged fish are being routed directly to the river.  The secondary (C and D) PIT-tag/bypass gates remain closed and off for fish collection.  Balloon tests revealed that PIT tag release lines were clear of any blockages this week.  Sample gates continued to function well.

Transport Summary:  As mentioned above, trucks left the McNary facility every day this week.  On September 15, the trailer’s left tail light was replaced.  On September 16, the trailer discharge hose was repaired.  This hose discharges excess water from the tanker when raceways are off loaded.  Drivers also noted during the pre-trip inspection that the truck tractor had a non-working tail light and faulty rear view mirror motor switch.  This tractor will be replaced with another leased tractor that is being held in reserve on project.

River Conditions

River conditions during the week are outlined in Table 1 as provide by the smolt monitoring staff whose data day runs from 0700 to 0700 hours each day.

Table 1.  River conditions at McNary Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF) |  | Water Clarity* (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 101.0 | 60.0 | 0.0 | 0.0 | 66.1 | 65.3 | 6.0 | 6.0 |

*Control room data.

Other

Inline Cooling Water Strainers:  Cooling water strainer inspections last took place on August 18 in turbine unit 6.  No salmonids, lamprey or other fish were noted.

Invasive Species: No invasive species were found during the September 1 detector inspection.  The next inspection is scheduled to take place October 1.

Predatory bird counts continued with tailwater and forebay observations being conducted twice and once daily, respectively.  The tailwater high counts included 37 gulls, 36 cormorants and 18 Forester’s Terns with an occasional pelican being noted.  Most tailwater birds were seen roosting in the spill basin and feeding in the powerhouse flow.  Bird counts appear to fluctuate with the juvenile shad outmigration.  An occasional gull or tern was seen around the bypass outfalls.  An occasional gull, cormorant or osprey was observed in the forebay.  No grebes were seen in the gatewell slots.  The three grebes noted in the collection channel at the end of the previous report period are still present.  Grebe removal may be coordinated with APHIS personnel in October.  The water cannon continued to operate satisfactory.

Project:  Ice Harbor

# Biologist: Mark Plummer

Dates:  September 10 - 16, 2010

## Turbine Operation

All turbine units (6) were available for operation during this reporting period.  Turbine unit 1 returned from annual maintenance September 11 at 1500 hours.  Turbine unit 2 went out of service for annual maintenance September 13 at 1015 hours. Turbine units 6, 5, 4, and 3 were out of service for short periods September 13 while STS inspections were performed.  Turbine unit 1 was out of service for a short period September 15 while the STS inspection was performed.

## Adult Fish Passage Facilities

### Fish facility personnel inspected the adult fishways September 10, 14, 15, and 16.

### Fish Ladders:  All north and south fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria.

### Fishway Entrances and Collection Channel (inspection date order):  The south shore entrance (SFE) was on sill with a depth of 9.1 feet, on sill with a depth of 8.7 feet, on sill with a depth of 8.7 feet, and off sill with a depth of 7.9 feet.  The north powerhouse entrance (NFE) was off sill with a depth of 7.7 feet, off sill with a depth of 7.7 feet, off sill with a depth of 7.9 feet, and off sill with a depth of 7.9 feet.  The north shore entrance (NSE) was off sill with a depth of 8.1 feet, off sill with a depth of 8.0 feet, off sill with a depth of 8.1 feet, and off sill with a depth of 7.8 feet.  Fishway entrance criterion is 8 feet depth, greater than 8 feet depth, or on sill.  All out of criteria depths were reported to the operator to make corrections.  All channel/tailwater differentials were in criteria.  Visual staff gage readings are reported in this report.

### Auxiliary Water Supply System:  2 of the 3 north shore fish pumps were operated without problems.  All north shore fish pumps are in service.  5 to 6 of 8 south shore fish pumps were operated.  South fish pumps are going in and out of service while motor replacement continued this period.  5 to 6 pumps are being operated to maintain criteria while replacement occurs.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There is minimal forebay debris.  Fish ladder exits are clear of debris and the bubblers are operating.

STSs/VBSs:  The STSs operation is in cycle run mode as of August 30.  No problems were found during the September STS/VBS inspections.  October STS/VBS inspections are scheduled for the 18th and 20th.

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe:   The juvenile fish bypass is in operation.  20 orifices are open.

Juvenile Bypass Facility:  The bypass was put in operation March 8, 2010.

Juvenile Fish Sampling:  Sampling for the 2010 season concluded July 1 due to the number of juvenile fish sampled during a 4 hour period dropping below 100 for 2 consecutive samples.

Removable Spillway Weir:  The RSW is not in operation.  Spill for fish passage ended September 1.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Ice Harbor Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 34.3 | 19.1 | 0.4 | 0.1 | 68 | 66 | 6.8 | 6.3 |

*Unit 1 scrollcase temperature.

Other

Inline Cooling Water Strainers:  Cooling water strainer cleanings took place in turbine units 4, 5 and 6 on August 9 and in turbine units 1, 2 and 3 on August 11.  No lampreys were found.

Invasive Species: No zebra mussels were observed during inspections performed on September 14.  However, several juvenile shad were found in the strainers.

Spill occurred for short periods on September 15 and 16 during spillway gate structural tests.

# Project:  Lower Monumental Dam

# Biologist(s):  William Spurgeon and Elizabeth Lindsey

Dates:  September 10 - 16, 2010

## Turbine Operation

Turbine units are being operated in hard constraint 1% operational criteria.  Turbine unit 1 was removed from service for annual maintenance on September 8 at 1015 hours.  Turbine unit 5 remains out of service as of August 10 at 0957 hours pending contractor evaluation.

Adult Fish Passage Facility

The adult fishway was inspected by Corps or State biologists on September 10, 11, 12, and 15.

Fish Ladders: Fishway exit head differential and depth over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively) on all inspections.  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively) on all inspections.

### Fishway Entrances and Collection Channel: NPE 1 and NPE 2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections.  North shore channel/tailwater head was in criteria (1’-2’) on all inspections.

SPE 1 and SPE 2 weir gates were in depth or sill criteria (criteria: > 8’ or on sill) on all inspections.  While on sill, the gate depth readings were 7.2’, 7.6’, 7.1’ and 7.0 feet.  South powerhouse channel/tailwater head was in criteria (1’-2’).

SSE1 weir gate was in depth or sill criteria (criteria: > 8’ or on sill) on all inspections.  While on sill, the gate depth reading was 7.9 feet.  SSE2 was in criteria (6’ above sill) on all inspections.  South shore channel/tailwater head was in criteria (1’-2’).

### Auxiliary Water Supply System: AWS pump 3 remains out of service to replace the bearing housing and repair the diffuser assembly.  This work is scheduled to be completed in September.  Pumps 1 and 2 were in service throughout this period.  Pump 3 remains “bulkheaded off” to minimize water loss during two-pump operation.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 5.0 square yards of forebay debris observed during this period.  Gatewell debris surface coverage ranged from 0-25 percent.  No oil was observed in gatewells.

STSs/VBSs:  STSs have been operating in cycle mode since August 10 when the average fork length of sub-yearling Chinook and/or sockeye exceeded 120mm.  STS inspections were conducted on September 4 and 5.  All screens passed inspection.

Orifices, Collection Channel, Dewatering Structure, Flume:  The collection channel is operating with 18 orifices open.

Collection Facility:  The primary dewaterer mechanical screen cleaner was removed from service on August 31 due to slipping of the travel cable.  The pneumatic screen cleaner (bubbler) is more than adequate for keeping the screen clean through the remainder of the season.  No other problems were observed in facility systems or operation.

Transport Summary:  Alternate day midi-tanker transport is occurring.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Monumental Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF)* |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 34.6 | 20.5 | 0.0 | 0.0 | 65.0 | 64.0 | 4.9 | 4.6 |

*Scrollcase temperatures.

#### Other

Inline Cooling Water Strainers:  Cooling water strainers were inspected September 1.  Thirteen shad and eleven Siberian prawns were recovered.  No lampreys were found.

Invasive Species:  There were no zebra mussels observed at the monitoring stations on September 10.

Summer spill operation was initiated at 0003 hours on June 21 and ended on September 1 at 0005 hours.

Project:  Little Goose

# Biologist(s):  George Melanson and Richard Weis

Dates:  September 10 - 16, 2010

## Turbine Operation

Turbine units 1 and 3 through 6 were available for power generation throughout this reporting period.  Turbine unit 2 was removed from service for annual maintenance on September 7 at 1337 hours.  There were no reports of turbine units operating outside the 1% of best efficiency.

## Adult Fish Passage Facility

COE and ODFW fisheries biologists performed measured inspections of the adult fishway September 10, 13 and 16.

Fish Ladder:  The ladder exit head differential ranged between 0 and 0.2 feet (criteria < 0.5 ft.).  Water depths over the weirs remained steady at 1.2 feet (criteria 1.0-1.3 ft.) and picketed lead head differentials ranged between 0 and 0.1 feet (criteria < 0.3 ft.).

Fishway Entrances and Collection Channel:  Channel to tailwater head differentials at fish entrances ranged between 1.58 and 1.72 (criteria 1.0 to 2.0 ft.).  SSE weir depths ranged between 8.28 and 8.34 feet (criteria ≥8.0 ft), NPE1 and 2 weirs rested on sill position through September 6.   Beginning September 7 NPE 1 and 2 lifted off sill.  NPE 1 ranged between 6.98 and 7.28 feet NPE 2 ranged between 6.98 and 7.30 feet.  (criteria ≥7.0 ft. or on sill).  NSE1 is manually positioned at 529.1 and depths measured between 6.28 and 10.54 feet (criteria ≥ 6.0 ft.).  NSE2 weir depth ranged between 6.12 and 6.16 feet (criteria ≥ 6.0 ft.).

Collection channel surface water velocities (criteria 1.5 to 4.0 fps) ranged between 1.8 and 2.3 fps near the SSE and 2.0 and 2.6 fps near the NSE.   Subsurface water velocities near the SSE (flowmeter) ranged between 1.3 and 1.6 fps.

Auxiliary Water Supply System:  All fish pumps operated within criteria during this report period.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Surface debris in the immediate forebay remained minimal during this report period.  Gatewells remain clear of debris.

Spillway Weir:  The weir was removed from service on August 5.

ESBS/VBS:   All operating ESBS were within criteria this report period.

Orifices, Collection Channel, Dewatering Structure, Flume:  The juvenile collection channel continued to operate with 23 open orifices – no problems to report.

Transportation Facility:  Collection and transport continued this report period.  Daily collection for the period ranged between 9 and 52 for a total of 142.  All fish were transported except for mortalities.  Descaling and mortality rates for this report period are 0.9% and 5.4% respectively.

Transport Summary:  Alternated day truck transport operations continued this report period.  Salt in small concentrations of approximately 1 g/L is added to the midi-tank water to treat potential Columnaris disease and reduce stress.  All transport operations were successfully performed.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Little Goose Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 27.9 | 14.7 | 0 | 0 | 66.5 | 64.3 | 5.8 | 4.8 |

*Ladder temperature.

Other

Cooling Water Strainers:  Cooling Water Strainers were inspected on Sept. 15.  No fish or lamprey was seen.

Invasive Species:  The Zebra Mussel substrate monitor was inspected on September 8, no mussels were observed.  The next inspection for zebra mussels is scheduled for October 6.

Avian Activity:  Up to 27 gulls and 8 cormorants were observed in the vicinity of the dam during this report period.

Project:  Lower Granite

# Biologist(s):  Mike Halter and Ches Brooks

Dates:  September 10 - 16, 2010

## Turbine Operation

Lower Granite had turbine units 1, 2, 5 and 6 available for power generation at the beginning of the report week.   Turbine unit 3 remained out of service for a rewind and will not be available until approximately December 31, 2010.  Turbine unit 4 remained out of service for annual maintenance.  The estimated return to service date is September 24.

## Adult Fish Passage Facility

On September 10-13, the Lower Granite fisheries biologists performed measured inspections of the adult fishway.

Fish Ladder:   All criteria were met during the report period.

Fishway Entrances and Collection Channel:   Head differential readings remained within criteria at all adult fishway entrances this week.  Weir depths at the south shore fishway entrances were also within criteria on all inspections this week.  North powerhouse fishway entrance weirs were within criteria on the September 10-12 inspections but on sill on the September 13 inspection due to tailwater levels dropping below 636.0 feet.   Weir depths at the north shore fishway entrances were out of criteria all week with readings of between 4.9 and 5.2 feet (criterion ≥ 7.0 feet).  Weir depth readings at the north shore are being sacrificed in order to maintain the requisite 1.0 foot of head differential.  Weekly velocity readings in the adult fishway collection channel transition pool area ranged from 0.81 to 1.02 feet per second and averaged 0.92 feet per second.

### Auxiliary Water Supply System:  Fish pumps 2 and 3 were operated during the week without any problems.

#### Juvenile Fish Passage Facility

The juvenile fish sample rate remained at the 100% level all week.

Forebay Debris/Gatewell Debris/Oil:  Debris levels were low during the week.  It was not necessary to hand-dip debris from any gatewells.   The oil film on the surface of bulkhead slot 4C has gradually been absorbed.  Oil soaker pads are in place.

ESBSs/VBSs:   The last ESBS/VBS video inspections took place on August 28-29.  No new problems were found on this month’s inspections.  The next inspections are scheduled for late September or early October.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:   Debris levels were very light during the week.  Collection gallery orifices were backflushed every three hours around the clock to ensure they remained free of materials that might impact fish passage.

Transportation Facility:   The facility operated in a 100% sampling mode with all collected fish being diverted to the sample holding tank outside the JFF lab.  Fish are being worked up every other day on designated transport dates.  All facets of facility operation continue to go smoothly.

Transport Summary:  Fish are being trucked on the odd days of the month.  Fish numbers remained low enough this week to utilize the pickup midi-tanker (300 gallon tank) on all trips.  Fish are being released into the outfall pipe below Bonneville Dam.  Transport operations have been going quite well.

Removable Spillway Weir:   Nothing new to report on the RSW.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Granite Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 27.6 | 24.0 | 0.0 | 0.0 | 64.0 | 63.3 | 5.0 | 5.0 |

*Cooling line intake temperature.

Other

Cooling Water Strainers: Inspection of the cooling line strainers took place on September 16.  One lamprey mort and one juvenile salmonid mort were noted.

Invasive Species:   The zebra mussel trap at the adult fishway exit was examined for zebra mussels on the September 6 inspection.  No evidence of zebra mussels was found.

Research:  The adult fish trap continued operation at a 12% sample rate during the report week.  (The sample rate will be lowered during the next report week due to hatcheries getting their brood stock too fast.)  One out of 25 hatchery steelhead and all wild PIT-tagged steelhead are being scale-sampled.  Scale samples and genetic samples are being taken from PIT-tagged steelhead.  Transport of adult fall Chinook to Lyon’s Ferry Hatchery and the Nez Perce Hatchery at Cherry Lane continued during the week. Seventy percent of the transported fish are being transported to Lyon’s Ferry and the remaining 30% are being transported to Cherry Lane.  The Nez Perce Tribe is hauling fish on Sundays and Mondays and Lyon’s Ferry personnel are hauling fish Tuesday through Saturday.