U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

#### FISH FACILITIES WEEKLY REPORT

#36-2010

# Project:  McNary

# Biologists: Bobby Johnson

Dates:  October 29 – November 4, 2010

## Turbine Operation

McNary had ten to twelve units available for power generation this week.  Units 2 and 7 remain out of service for a rewind contract until year’s end.  On October 29, unit 1 returned to service with the completion of the transformer T1 replacement contract and testing.  On November 1, unit 8 was removed from service for relay upgrades.  The unit is scheduled to return on December 10.  From November 2 to 3, unit 13 was out of service due to a headgate hydraulic fluid leak in 13A slot.  Also, on November 2, unit 9 was out of service 26 minutes for ESBS camera inspection.  On November 3, unit 9 was out of service three hours for replacement of the VBS in 9C slot.  The hard one percent criterion concluded November 1.  No units ran outside the criteria before then.  On November 4, units ran briefly outside the soft criteria during VBS cleaning.

## Adult Fish Passage Facilities

On October 31, November 2 and 4, the McNary fisheries biologist performed measured inspections of the adult fishways.  Adult fish counting season concluded the evening of October 31.  With counters no longer available to help monitor the picketed leads and both ladder exits having issues with the equipment needed to raise the leads for cleaning, on November 1, the picketed leads were raised for the winter season.  On November 14, the adult lamprey passage study, for which Oregon entrance weirs SFEW1, SFEW2 and NFEW1 are lowered on scheduled nights, will conclude.

Fish Ladders:  During measured inspections, all Fish Passage Plan criteria were met on both ladders.  At the Washington exit, the regulating weir alarmed once and was reset with the tilting weirs also being adjusted.  A low water alarm also occurred which was reset.  At the Oregon exit, the north traveling screen remains out of service.  On October 31, the south traveling screen was noted not be rotating.  Operators found on problem.  On November 3, the screen was found to be slipping on a gear and was removed from service.  The next day, mechanics resolved the issue and returned the screen to service.

Fishway Entrances and Collection Channel:  At the Washington ladder, all inspection points were in criteria.  On November 2 and 4, Oregon entrance weir SFEW1 measured 8.9 feet each day.  All other Oregon ladder inspection points were in criterion.  The collection channel velocity average 1.5 feet per second.

Auxiliary Water Supply System:  For the week, two or three fish pumps were operational with blade angles of 30 or 22 degrees with interruptions described below.  On October 29, pump 3 returned to service with the conclusion of the replacement transformer T1.  The return of pump 3 has improved the north powerhouse pool differential.  On November 1 at 0940, pump 1 tripped off line during a power transfer.  At 1323, after a coil was replaced, the pump returned to service.  On November 2 at 0933, all three pumps were removed from service for DC ground work.  At 0944, pumps 1 and 2 returned to service.  On November 3 at 1015, pump 3 returned to service after a ground repair.  On November 4 at 0130, pump 3 was removed from service due to an oil leak.  The pump will return to service early next week.  The juvenile facility supplied the usual 450 cfs to the north powerhouse pool with no interruption.  Finally, on October 31 from 1454 to 1553, the Wasco County PUD unit had one interruption with no reason found and the bypass system operating well.

### Juvenile Fish Passage Facility

Fall primary bypass season continues with PIT tag detection occurring in the full flow flume.  No changes in facility operations occurred.  The system will remain watered up to avoid possible freeze breakage which may occur before winter maintenance season begins in December.

Forebay Debris/Gate well Debris/Oil:  Forebay debris was light and consisted of mostly Eurasian milfoil and woody debris.  Trash rack differentials revealed no problems and no racks were cleaned.  For the maintenance contract on the forebay deck crane, the slots at 14A, 14B and 14C remain covered.  On November 2, hydraulic fluid for the headgate in 13A slot was observed on the water’s surface.  The unit was immediately removed from service and unit 13’s channel orifices were closed.  By November 3, absorbent pads and booms along with a skimmer had removed the oil allowing the unit and orifices to return to service.  No other problems were observed in the gatewell slots.

ESBSs/VBSs:  ESBS’s are installed at all units.  The screens at 5A, 5C, 9C and 10C slots remain in transducer bypass mode.  ESBS camera inspections at units 8 and 9 revealed no problems.  On November 3, as part of the VBS rehabilitation program, the screen at 9C slot was cleaned and replaced.  On November 3 and 4, VBS monitoring revealed four screens out of criteria.  These screens and three others were cleaned.  The VBS in 1A slot has a bent frame and can only be partly cleaned with a portable crane as the deck crane remains out of service into mid-November.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  For the week, 40 to 41 orifices were in use depending on forebay elevation.  The orifices at unit 2, which is out of service, continue to be opened or closed as required.  On October 31, a stick was removed from the orifice flow at 5B slot.  As mentioned above, from November 3 to 4, the orifices at unit 13 were closed due to the hydraulic fluid leak in 13A slot.  During this time, makeup orifices were used at unit 12.  No other problems occurred with all systems operating well in automatic mode.

Transportation Facility:  The facility remains shut down for fall primary bypass season.  All systems are off for the year.  Little maintenance along with safety modifications will be preformed at the facility until winter season begins.  On October 29, with the transformer T1 contract completed, the facility had an uneventful 20 minute power outage associated with bring T1 back to service.  The facilities’ shop received a new heat pump.

Transport Summary:  There is nothing to report.  Winter maintenance on the fish trailers continues.

River Conditions

River conditions during the week are outlined in Table 1 as provide by the control room as the smolt monitoring staff is no longer collecting data.  The control room data day runs from 0000 to 0000 each day.

Table 1.  River conditions at McNary Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 126.6 | 81.7 | 0.0 | 0.0 | 58 | 55 | 6.0 | 6.0 |

Other

Inline Cooling Water Strainers:  No cooling water strainer inspections took place this week.

Invasive Species: The zebra mussel station examination on November 2 revealed no problems.

Casual observations of the tail water area revealed gulls, mergansers and cormorants.  Most birds were seen roosting near the spill basin or feeding in the powerhouse flow.  Bird numbers appear to be fluctuating with juvenile shad out migration.  At the bypasses’ out falls, occasional mergansers, cormorants and gulls were noted.  The water cannon operated well.  In the forebay area, groups of grebes were noted along with the occasional gull or cormorant.  The grebe observed in the gatewell slot last week passed into the channel and out of the system.

Project:  Ice Harbor

# Biologist Science Technician:  Steve Jeffers

Dates:  October 29 – November 4, 2010

## Turbine Operation

Turbine units 1, 2, and 4 - 6 were available for operation this reporting period.  Turbine unit 3 remained out of service for overhaul.

## Adult Fish Passage Facilities

### Fish facility personnel inspected the adult fishways November 1, 2, 3, and 4.

### Fish Ladders:  All north and south fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria. Over the weir criteria is 1.0 – 1.3 feet.

### Fishway Entrances and Collection Channel (inspection date order):  The south shore entrance (SFE) was off sill with a depth of 7.8 feet, off sill with a depth of 7.9 feet, off sill with a depth of 7.9 feet, and off sill with a depth of 8.0 feet.  The north powerhouse entrance (NFE) was off sill with a depth of 8.0 feet, on sill with a depth of 7.8 feet, on sill with a depth of 8.0 feet, and off sill with a depth of 8.0 feet.  The north shore entrance (NSE) was off sill with a depth of 7.6 feet, on sill with a depth of 7.8 feet, on sill with a depth of 7.9 feet, and on sill with a depth of 8.0 feet.  Fishway entrance criterion is 8 feet depth, greater than 8 feet depth, or on sill.  All of the out of criteria fish entrance depths were reported to the shift operator to make adjustments or initiate a trouble report.  All channel/tailwater differentials were in criteria.  Visual staff gage or measuring tape readings are reported in this report.

### Auxiliary Water Supply System:  2 of the 3 north shore fish pumps were operated without problems.  5 of 8 south shore fish pumps were operated without problems.  South shore fish pump 1 remains out of service due to vibration.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There is minimal forebay debris.  Fish ladder exits are clear of debris and the bubblers are operating.

STSs/VBSs:  The STSs operation is in cycle run mode.  No problems were found during the October STS/VBS inspections.  November STS/VBS inspections are scheduled for the 15 and 17.

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe:   The juvenile fish bypass is in operation.  20 orifices are open.

Juvenile Bypass Facility:  The bypass was put in operation March 8, 2010.

Juvenile Fish Sampling:  Sampling for the 2010 season concluded July 1 due to the number of juvenile fish sampled during a 4 hour period dropping below 100 for 2 consecutive samples.

Removable Spillway Weir:  The RSW is not in operation.  Spill for fish passage ended September 1.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Ice Harbor Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 25.9 | 17.9 | 0.0 | 0.0 | 58 | 57 | 6.9 | 6.2 |

*Unit 1 scrollcase temperature.

Other

Inline Cooling Water Strainers:  Main turbine units cooling water strainer inspections are performed during STS/VBS inspections.

Invasive Species:  No zebra mussels were observed when the inspection was performed November 1.

The water velocity meter located in the south adult fishway is not functioning.  Repairs/replacement will be done during the adult fish winter maintenance period.

No adult salmonid mortalities observed this reporting period.

# Project:  Lower Monumental Dam

# Biologist(s):  William Spurgeon and Elizabeth Lindsey

Dates:  October 29 – November 4, 2010

## Turbine Operation

Turbine units were operated in hard constraint 1% operational criteria through October 31 and in soft constraint thereafter.  Unit 4 was removed from service for annual maintenance on October 13 at 0714 hours and returned to service on October 30 at 1130 hours.  Unit 5 was removed from service for annual maintenance on November 1 at 0730 hours.

Adult Fish Passage Facility

The adult fishway was inspected by Corps biologists on November 1, 2, and 3.

Fish Ladders: Fishway exit head differential and depth over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively) on all inspections.  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively) on all inspections.

### Fishway Entrances and Collection Channel:  NPE 1 and NPE 2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections.  North shore channel/tailwater head was in criteria (1’-2’) on all inspections.

SPE 1 and SPE 2 weir gates were in sill criteria (criteria: > 8’ or on sill) on all inspections.  While on sill, the gate depth readings were 7.3’, 6.5’, and 7.0 feet.  South powerhouse channel/tailwater head was in criteria (1’-2’).

SSE1 weir gate was in depth criteria or sill criteria (criteria: > 8’ or on sill) on all inspections.  While one sill, the gate depth reading was 7.3 feet.  SSE2 was in criteria (6’ above sill) on all inspections.  South shore channel/tailwater head was in criteria (1’-2’).

### Auxiliary Water Supply System:  AWS pump 3 remains out of service to replace the bearing housing and repair the diffuser assembly.  Pumps 1 and 2 were in service throughout this period.  Pump 3 is bulkheaded off to minimize water loss during two-pump operation.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 18.3 square yards of forebay debris observed during this period.  Gatewell debris surface coverage was out of criteria on the November 1 inspection with 65% and 70% coverage on slots 2A and 2B, respectively.  Gatewell slots were dipped on November 2.  No oil was observed in gatewells.

STSs/VBSs:  STS operation was changed to cycle mode on August 10 as average fork length of sub-yearling chinook and/or sockeye exceeded 120mm.  The final STS inspection for 2010 was conducted on November 1 and 2.  All screens passed inspection.

Orifices, Collection Channel, Dewatering Structure, Flume:  The collection channel is operating with 18 to 19 orifices open.  The primary dewaterer automatic switch gates have been continuously cycling up and down outside of the optimal water level range.  The gates were manually set to maintain 528.0 feet on October 21 and remain in the off position.

Collection Facility:  The primary dewaterer mechanical screen cleaner was removed from service on August 31 due to slipping of the travel cable.  The pneumatic screen cleaner is more than adequate for keeping the screen clean through the remainder of the season.  Facility operation changed to primary bypass on October 1.  The load and hold facility is in winter maintenance mode.

Transport Summary:  Transport ended October 1.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Monumental Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF)* |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 24.3 | 17.5 | 0.0 | 0.0 | 58.5 | 58.0 | 5+ | 5.0 |

*Scrollcase temperatures.

#### Other

Inline Cooling Water Strainers:  Unit cooling water strainers were cleaned on November 1 (Table 2).

Table 2.  Unit cooling water strainer inspection.  Aquatic organisms recovered.

|  | Lamprey |  | Salmon |  | Steelhead |  | Siberian Prawn |  | Shad |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Unit | Live | Dead | Live | Dead | Live | Dead | Live | Dead | Live | Dead |
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 |
| 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 |
| 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 |
| 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 20 |
| 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 |

Invasive Species:  There were no zebra mussels observed at the monitoring stations on October 14.

Project:  Little Goose

# Biologist(s):  George Melanson

Dates:  October 29 – November 4, 2010

## Turbine Operation

Turbine units 1 through 5 were available for power generation throughout this reporting period.    Turbine unit 6 was placed out of service for its 6 year overhaul on October 18.   There were no reports of turbine units operating outside the 1% of best efficiency.

## Adult Fish Passage Facility

ODFW and COE Fisheries Biologists performed measured inspections of the adult fishway October 29, November 2 and 3.

Fish Ladder:  The ladder exit head differential held steady at 0.1 feet (criteria < 0.5 ft.).  Water depths over the weirs ranged between 1.1 and 1.2 feet (criteria 1.0-1.3 ft.) and head differentials between picketed leads were negligible at 0 feet (criteria < 0.3 ft.).

Fishway Entrances and Collection Channel:  Channel to tailwater head differentials at fish entrances ranged between 0.94 and 1.62 (criteria 1.0 to 2.0 ft.).  SSE weir depths ranged between 8.20 and 8.32 feet (criteria ≥8.0 ft),   NPE weir depths ranged between 6.80 feet (sill) and 7.28 feet (criteria ≥7.0 ft. or on sill).  NSE1 is manually positioned at 529.1 and depths measured between 9.38 and 10.30 feet (criteria ≥ 6.0 ft.).  NSE2 weir depth ranged between 6.16 and 6.22 feet (criteria ≥ 6.0 ft.).

Collection channel surface water velocities (criteria 1.5 to 4.0 fps) ranged between 1.6 and 2.4 fps near the SSE and 2.5 and 3.1 fps near the NSE.   Subsurface water velocities near the SSE (flowmeter) ranged between 1.1 and 1.4 fps.

Auxiliary Water Supply System:  All fish pumps operated within criteria during this report period.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Surface woody debris in the immediate forebay ranged between 900 and 1200 square feet.   Gatewells remain clear of debris.

Spillway Weir:  The weir was removed from service on August 5.

ESBS/VBS:   All operating ESBS were within criteria this report period.

Orifices, Collection Channel, Dewatering Structure, Flume:  The collection channel operated with 20 open orifices during this report period.  No problems to report.

Transportation Facility:  Collection and transport continued through October 31.  The facility switched to primary bypass operations on October 31 at 0700 hours.   The 3 day collection for this period ranged between 152 and 429 for a total of 987.   Descaling and mortality rates for this report period are 0.94% and 3.85% respectively.

The facility was de-watered on November 1, winter maintenance is now in progress.

Transport Summary:  Fish were transported on alternate days with the last transport for the season occurring on October 31.   Salt in small concentrations of approximately 1 - 2 g/L was added to the midi-tank water to treat potential Columnaris disease and reduce stress.  All transport operations were successfully performed.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Little Goose Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 20.5 | 14.2 | 0 | 0 | 58.8 | 56.9 | 6.0+ | 6.0 |

*Ladder temperature.

Other

Inline Cooling Water Strainers:  Cooling Water Strainers were inspected on Oct. 3 and no fish or Lamprey observed.

Invasive Species:  The Zebra Mussel substrate monitor was inspected on November 3, no mussels were observed.  The next inspection for zebra mussels is scheduled for December 1.

Avian Activity:   Observations included up to 46 gulls and 31 cormorants.

Project:  Lower Granite

# Biologist(s):  Mike Halter and Ches Brooks

Dates:  October 29 – November 4, 2010

## Turbine Operation

Lower Granite had turbine units 1, 2, 5 and 6 available for power generation at the beginning of the report week.   Turbine unit 3 remained out of service for a rewind and will not be available until approximately January 28, 2011.  Turbine unit 1 was taken out of service for annual maintenance on November 1 and is scheduled to return to service on December 3.  Turbine unit 4 remained out of service for annual maintenance.  The estimated return to service date is November 19.   Alignment problems could extend this outage.

## Adult Fish Passage Facility

On October 29-30 and November 2-3 the Lower Granite fisheries biologists performed measured inspections of the adult fishway system.

Fish Ladder:   All criteria were met during the report period.

Fishway Entrances and Collection Channel:   Head differential readings remained within criteria at all adult fishway entrances during the weekly inspections.  Weir depths at the south shore and north powerhouse fishway entrances were also within criteria on all inspections this week due to the tailwater elevation exceeding 636.0 feet.  Weir depths at the north shore fishway entrances were out of criteria all week with readings of between 5.0 and 5.1 feet (criterion ≥ 7.0 feet).  Weir depth readings at the north shore entrances are being sacrificed in order to maintain the requisite 1.0 foot of head differential.  Weekly velocity readings in the adult fishway collection channel transition pool area ranged from 0.85 to 1.04 feet per second and averaged 0.94 feet per second.

### Auxiliary Water Supply System:  Fish pumps 2 and 3 were operated during the week without any problems.  Fish pump 1 is under clearance for repair to the lower bearings and parts are on order.  The availability date is uncertain at this time.

#### Juvenile Fish Passage Facility

The juvenile fish sample rate remained at the 100% level until 0700 hours on October 31 when the system was switched to secondary bypass (all juvenile fish routed out the pipe to mid-river release).  The system will operate in that mode through December 15.

Forebay Debris/Gatewell Debris/Oil:  Debris levels were low during the week.  It was not necessary to hand-dip debris from any gatewells.

ESBSs/VBSs:   The last ESBS/VBS video inspections of the year took place on October 21-22.  No new problems were found during this inspection.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:   Debris levels were very light during the week.  Collection gallery orifices were backflushed every three hours around the clock to ensure they remained free of materials that might impact fish passage.

Transportation Facility:   The facility operated in a 100% sampling mode until 0700 hours on October 31.  At that time the system was switched to secondary bypass (all fish back to the river through the mid-river release pipe).  This activity will continue until December 15 (weather permitting).  The separator complex is still being manned 24/7 due to fish being routed over the separator bars.  No PIT-tag detection system is available at Lower Granite unless fish are diverted through the separator.  Operation of the separator in secondary bypass mode will allow the detection of PIT-tagged juvenile fish (primarily subyearling chinook) to help determine late season movement patterns.

Transport Summary:  Fish were trucked on the odd days of the month.  Fish numbers were low enough to utilize the pickup midi-tanker (300 gallon tank) on both trips this report week.  Fish were released into the outfall pipe below Bonneville Dam.  All transport operations concluded on October 31.

Removable Spillway Weir:   Nothing new to report on the RSW.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Granite Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 23.0 | 17.7 | 0.0 | 0.0 | 58 | 55 | 5.0 | 5.0 |

*Cooling line intake temperature.

Other

Inline Cooling Water Strainers:   Inspection of the cooling line strainers last took place on October 14.  Two lamprey mortalities were noted.

Invasive Species:   The zebra mussel trap at the adult fishway exit was examined for zebra mussels on the October 29 inspection.  No evidence of zebra mussels was found.

Research:  The sample rate at the adult fish trap remained at 10% during the report week.  In addition, the protocol for taking scale samples from hatchery steelhead remained at one in 20 fish.  PIT-tagged chinook are still being released back into the ladder following an operculum punch.  Transport of adult fall chinook to Lyon’s Ferry Hatchery continued during the week.  Fish are being transported to Lyon’s Ferry when numbers warrant (approximately one load every week at this time).  The Nez Perce Hatchery at Cherry Lane met their quota for the year some time ago and no longer is transporting fall Chinook.

NOAA-Fisheries personnel continued PIT-tagging subyearling Chinook in the juvenile fish facility lab to evaluate late season truck transport operations at Lower Granite.  This operation concluded with the end of sampling activities on October 31.

USGS/BRD staff continued radio-tagging juvenile subyearling Chinook (taken from the samples) in the lab through October 29.  Fish were tagged to evaluate subyearling Chinook juvenile migration patterns during the late fall including use of habitat areas.  Approximately 175 subyearlings were  radio-tagged for this study.   This week a total of 54 subyearling fall Chinook were radio and PIT-tagged and released at Offield Landing.  An additional three fish were not tagged and also released at Offield.