U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

#### FISH FACILITIES WEEKLY REPORT

#37-2010

# Project:  McNary

# Biologists: Bobby Johnson

Dates:  November 5 - 11, 2010

## Turbine Operation

McNary had eleven units available for power generation this week.  Units 2 and 7 remain out of service for a rewind contract until year’s end.  Unit 8 was remains out service for relay upgrades until December 10.  On November 9, units 10 and 11 were out of service for a total of 43 minutes for ESBS camera inspections.  On November 8, the load on unit 1 was reduced to the lower end of the soft one percent criterion due to a high VBS differential on the screen in 1A slot.  The frame on this VBS is bent and the screen cannot be moved with a portable crane therefore the unit will have to remain at a reduced load until the intake deck crane returns to service and the VBS is cleaned.

## Adult Fish Passage Facilities

On November 9 and 10, the McNary fisheries biologist performed measured inspections of the adult fishways.  On November 14, the adult lamprey passage study, for which Oregon entrance weirs SFEW1, SFEW2 and NFEW1 are lowered on scheduled nights, will conclude.  This week, the RAM (random access memory) for the count station computers was increased.

Fish Ladders:  During measured inspections, all Fish Passage Plan criteria were met on both ladders.  At the Washington exit, the tilting weirs were adjusted.  At the Oregon exit, the north traveling screen remains out of service.  No problems occurred at either exit.

Fishway Entrances and Collection Channel:  At both ladders, all inspection points were in criteria.  Though not affecting criteria, on November 8, shorted wiring at the Washington entrance weirs was repaired.  The Oregon ladder’s collection channel velocity averaged 1.3 feet per second.

Auxiliary Water Supply System:  For the week, two or three fish pumps were operational with blade angles of 30 or 22 degrees.  On November 8, pump 3 returned to service after the oil head was repacked.  On November 11 at 2345, pump 3 tripped off line due to a bearing issue.  The problem will be examined and resolved early next week.  The juvenile facility supplied the usual 450 cfs to the north powerhouse pool with no interruption.  Finally, on November 6 from 2022 to 2130 and November 8 from 1702 to 1809, the Wasco County PUD unit had two interruptions with no reason reported.  During each interruption, the bypass system operated well.

### Juvenile Fish Passage Facility

Fall primary bypass season continues with PIT tag detect occurring in the full flow flume.  No changes in facility operations occurred.  The system will remain watered up to avoid possible freeze breakage which may occur before winter maintenance season begins in December.

Forebay Debris/Gate well Debris/Oil:  Forebay debris was light and consisted of mostly Eurasian milfoil and woody debris.  Trash rack differentials revealed no problems and no racks were cleaned.  For the maintenance contract on the forebay deck crane, the slots at 14A, 14B and 14C remain covered.  No problems were observed in the gatewell slots.

ESBSs/VBSs:  ESBS’s are installed at all units.  The screens at 5A, 5C, 9C and 10C slots remain in transducer bypass mode.  ESBS camera inspections at units 10 and 11 revealed no problems.  On November 8, as mentioned above, the VBS at 1A slot measured out of criteria resulting in the unit’s load being reduced until the deck crane returns to service into mid-November.  On November 10, four VBS’s were cleaned as a preventative measure.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  For the week, 41 orifices were in due to a stable forebay elevation.  The orifices at unit 2, which is out of service, continue to be opened or closed as required.  No problems occurred with all systems operating well in automatic mode.

Transportation Facility:  The facility remains shut down for fall primary bypass season.  All systems are off for the year.  Little maintenance along with safety modifications will be preformed at the facility until winter season begins.  Work on the facilities’ heating and cooling system continues.

Transport Summary:  There is nothing to report.  Winter maintenance on the fish trailers continues.

River Conditions

River conditions during the week are outlined in Table 1 as provide by the control room as the smolt monitoring staff is no longer collecting data.  The control room data day runs from 0000 to 0000 each day.  The spillway hoists received scheduled maintenance this week.

Table 1.  River conditions at McNary Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 128.0 | 89.1 | 0.0 | 0.0 | 57 | 56 | 6.0 | 6.0 |

Other

Inline Cooling Water Strainers:  No cooling water strainer inspections took place this week.

Invasive Species: The zebra mussel station examination on November 2 revealed no problems.  The next zebra mussel station examination will be in early December.

Casual observations of the tail water area revealed gulls, mergansers and cormorants.  Most birds were seen roosting near the spill basin or feeding in the powerhouse flow.  Bird numbers appear to be fluctuating with juvenile shad out migration.  At the bypasses’ out falls, occasional mergansers, cormorants and gulls were noted.  The water cannon operated well.  In the forebay area, groups of grebes were noted along with the occasional gull or cormorant.  No grebes were observed elsewhere in the system.

Project:  Ice Harbor

# Biologist:  Mark F. Plummer

Dates:  November 5 - 11, 2010

## Turbine Operation

Turbine units 1, 2, and 4 - 6 were available for operation this reporting period.  Turbine unit 3 remained out of service for overhaul.  Turbine unit 4 went out of service for blade inspection November 8 at 0614 hours.

## Adult Fish Passage Facilities

### Fish facility personnel inspected the adult fishways November 5, 8, and 10.

### Fish Ladders:  All north and south fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria. Over the weir criteria is 1.0 – 1.3 feet.  The north and south picketed leads were put in the raised position due to adult fish counting ending October 31.

### Fishway Entrances and Collection Channel (inspection date order):  The south shore entrance (SFE) was on sill with a depth of 8.0 feet, on sill with a depth of 7.5 feet, and on sill with a depth of 7.6 feet.  The north powerhouse entrance (NFE) was on sill with a depth of 7.8 feet, on sill with a depth of 7.3 feet, and on sill with a depth of 7.4 feet.  The north shore entrance (NSE) was on sill with a depth of 7.7 feet, on sill with a depth of 7.2 feet, and on sill with a depth of 7.2 feet.  Fishway entrance criterion is 8 feet depth, greater than 8 feet depth, or on sill.  All channel/tailwater differentials were in criteria.  Visual staff gage or measuring tape readings are reported in this report.

### Auxiliary Water Supply System:  2 of the 3 north shore fish pumps were operated without problems.  5 of 8 south shore fish pumps were operated without problems.  South shore fish pump 1 remains out of service due to vibration.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There is minimal forebay debris.  Fish ladder exits are clear of debris and the bubblers are operating.

STSs/VBSs:  The STSs operation is in cycle run mode.  No problems were found during the October STS/VBS inspections.  November STS/VBS inspections are scheduled for the 15 and 17.

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe:   The juvenile fish bypass is in operation.  20 orifices are open.

Juvenile Bypass Facility:  The bypass was put in operation March 8, 2010.

Juvenile Fish Sampling:  Sampling for the 2010 season concluded July 1 due to the number of juvenile fish sampled during a 4 hour period dropping below 100 for 2 consecutive samples.

Removable Spillway Weir:  The RSW is not in operation.  Spill for fish passage ended September 1.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Ice Harbor Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 27.1 | 11.1 | 0.0 | 0.0 | 57 | 55 | 7.2 | 6.4 |

*Unit 1 scrollcase temperature.

Other

Invasive Species:  No zebra mussels were observed when the inspection was performed November 5, 8, and 10.

Inline Cooling Water Strainers:  Main turbine units cooling water strainer inspections are performed during STS/VBS inspections.   We are currently finding many juvenile shad mortalities in the strainers.

The water velocity meter located in the south adult fishway is not functioning.  Repairs/replacement will be done during the adult fish winter maintenance period.

No adult salmonid mortalities observed this reporting period.

# Project:  Lower Monumental Dam

# Biologist(s):  William Spurgeon and Elizabeth Lindsey

Dates:  November 5 - 11, 2010

## Turbine Operation

Turbine units are being operated in soft constraint of the 1% operational criteria.  Unit 5 was removed from service for annual maintenance on November 1 at 0730 hours.

Adult Fish Passage Facility

The adult fishway was inspected by Corps biologists on November 8, 9, and 10.

Fish Ladders: Fishway exit head differential and depth over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively) on all inspections.  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively) on all inspections.  Picketed leads were raised for the winter on November 4.

### Fishway Entrances and Collection Channel: NPE 1 and NPE 2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections.  North shore channel/tailwater head was in criteria (1’-2’) on all inspections.

SPE 1 and SPE 2 weir gates were in sill criteria (criteria: > 8’ or on sill) on all inspections.  While on sill, the gate depth readings were 7.5’, 7.3’, and 7.2 feet.  South powerhouse channel/tailwater head was in criteria (1’-2’).

SSE1 weir gate was in depth criteria or sill criteria (criteria: > 8’ or on sill) on all inspections.  While one sill, the gate depth reading was 7.7 feet.  SSE2 was in criteria (6’ above sill) on all inspections.  South shore channel/tailwater head was in criteria (1’-2’).

### Auxiliary Water Supply System: AWS pump 3 remains out of service to replace the bearing housing and repair the diffuser assembly.  Pumps 1 and 2 were in service throughout this period.  Pump 3 is bulkheaded off to minimize water loss during two-pump operation.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 29.7 square yards of forebay debris observed during this period.  Gatewell debris ranged from 0 - 55% surface coverage.  Slot 3A was dipped on November 8 when it was found to have exceeded the 50% debris criteria.  No oil was observed in gatewells.

STSs/VBSs:  STS operation was changed to cycle mode on August 10 as average fork length of sub-yearling chinook and/or sockeye exceeded 120mm.  The final STS inspection for 2010 was conducted on November 1 and 2.  All screens passed inspection.

Orifices, Collection Channel, Dewatering Structure, Flume:  The collection channel is operating with 18 orifices open.  The primary dewaterer automatic switch gates have been continuously cycling up and down outside of the optimal water level range.  The gates were manually set to maintain 528.0 feet on October 21 and remain in the off position.

Collection Facility:  The primary dewaterer mechanical screen cleaner was removed from service on August 31 due to slipping of the travel cable.  The pneumatic screen cleaner is more than adequate for keeping the screen clean through the remainder of the season.  Facility operation changed to primary bypass on October 1.  The load and hold facility is in winter maintenance mode.

Transport Summary:  Transport ended October 1.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Monumental Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF)* |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 26.4 | 12.3 | 0.0 | 0.0 | 56.5 | 55.5 | 5+ | 4.6 |

*Scrollcase temperatures.

#### Other

Inline Cooling Water Strainers: Unit cooling water strainers were cleaned on November 1 (Table 2).

Table 2.  Unit cooling water strainer inspection.  Summary aquatic organisms recovered.

|  | Lamprey |  | Salmon |  | Steelhead |  | Siberian Prawn |  | Shad |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Unit | Live | Dead | Live | Dead | Live | Dead | Live | Dead | Live | Dead |
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 |
| 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 |
| 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 |
| 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 20 |
| 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 |

Invasive Species:  No zebra mussels were observed at the monitoring stations on November 8.

Project:  Little Goose

# Biologist(s):  George Melanson

Dates:  November 5 - 11, 2010

## Turbine Operation

Turbine units 1 through 5 were available for power generation throughout this reporting period.    Turbine unit 6 was placed out of service for its 6 year overhaul on October 18.   There were no reports of turbine units operating outside the 1% of best efficiency.

## Adult Fish Passage Facility

ODFW and COE Fisheries Biologists performed measured inspections of the adult fishway November 6, 8 and 10.

Fish Ladder:  The ladder exit head differential ranged between 0.1 and 0.2 feet (criteria < 0.5 ft.).  Water depths over the weirs ranged between 1.1 and 1.2 feet (criteria 1.0-1.3 ft.) and head differentials between picketed leads were negligible at 0 feet (criteria < 0.3 ft.).

Fishway Entrances and Collection Channel:  Channel to tailwater head differentials at fish entrances ranged between 0.98 and 1.56 feet (criteria 1.0 to 2.0 ft.).  SSE weir depths ranged between 8.26 and 8.38 feet (criteria ≥8.0 ft),   NPE weir depths ranged between 6.22 feet (sill) and 7.32 feet (criteria ≥7.0 ft. or on sill).  NSE1 is manually positioned at 529.1 and depths measured between 9.24 and 10.40 feet (criteria ≥ 6.0 ft.).  NSE2 weir depth ranged between 6.16 and 6.20 feet (criteria ≥ 6.0 ft.).

Collection channel surface water velocities (criteria 1.5 to 4.0 fps) ranged between 1.5 and 2.3 fps near the SSE and 2.1 and 2.7 fps near the NSE.   Subsurface water velocities near the SSE (flowmeter) ranged between 1.1 and 1.3 fps.

Auxiliary Water Supply System:  All fish pumps operated within criteria during this report period.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Surface woody debris in the immediate forebay ranged between 100 and 2000 square feet.   Gatewells remain clear of debris.

Spillway Weir:  The weir was removed from service on August 5.

ESBS/VBS:   All operating ESBS were within criteria this report period.

Orifices, Collection Channel, Dewatering Structure, Flume:  The collection channel operated with 20 open orifices during this report period.  No problems to report.

Transportation Facility:  The facility switched to primary bypass operations on October 31 at 0700 hours.   All fish are routed to the tailrace mid-channel area.  Seasonal maintenance work at the facility is in progress.

Transport Summary:  Fish transport ended on October 31.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Little Goose Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 24.0 | 13.5 | 0 | 0 | 55.9 | 54.8 | 6.0+ | 6.0 |

*Ladder temperature.

Other

Inline Cooling Water Strainers:  Cooling Water Strainers were inspected on Oct. 3 and no fish or lamprey observed.

Invasive Species:  The Zebra Mussel substrate monitor was inspected on November 3, no mussels were observed.  The next inspection for zebra mussels is scheduled for December 1.

Avian Activity:   Observations included up to 30 gulls and 10 Cormorants.

Project:  Lower Granite

# Biologist(s):  Mike Halter and Ches Brooks

Dates:  November 5 - 11, 2010

## Turbine Operation

Lower Granite had turbine units 2, 5 and 6 available for power generation at the beginning of the report week.   Turbine unit 3 remained out of service for a rewind and will not be available until approximately March 18, 2011.  Turbine unit 1 was taken out of service for annual maintenance on November 1 and is scheduled to return to service on December 3.  Turbine unit 4 remained out of service for annual maintenance.  The estimated return to service date is November 19.   Bearing alignment problems could extend this outage.

## Adult Fish Passage Facility

On November 8-10 the Lower Granite fisheries biologists performed measured inspections of the adult fishway system.

Fish Ladder:   All criteria were met during the report period.

Fishway Entrances and Collection Channel:   Head differential readings remained within criteria at all adult fishway entrances during the weekly inspections.  Weir depths at the south shore and north powerhouse fishway entrances were also within criteria on all inspections this week due to the tailwater elevation exceeding 636.0 feet.  Weir depths at the north shore fishway entrances were out of criteria all week with readings of between 5.0 and 5.1 feet (criterion ≥ 7.0 feet).  Weir depth readings at the north shore entrances are being sacrificed in order to maintain the requisite 1.0 foot of head differential.  Weekly velocity readings in the adult fishway collection channel transition pool area ranged from 0.85 to 1.04 feet per second and averaged 0.94 feet per second.

### Auxiliary Water Supply System:  Fish pumps 2 and 3 were operated during the week without any problems.  Fish pump 1 is under clearance (bulkheaded off) for repair to the lower bearings and parts are on order.  The availability date is uncertain at this time.

#### Juvenile Fish Passage Facility

The juvenile fish sample rate remained at the 100% level until 0700 hours on October 31 when the system was switched to secondary bypass (all juvenile fish routed out the pipe to mid-river release).  The system will operate in that mode through December 15.

Forebay Debris/Gatewell Debris/Oil:  Debris levels were low during the week.  It was not necessary to hand-dip debris from any gatewells.

ESBSs/VBSs:   The last ESBS/VBS video inspections of the year took place on October 21-22.  No new problems were found during this inspection.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:   Debris levels were variable during the week.  A clog developed in the secondary bypass line on the morning of November 8.  JFF maintenance personnel were able to clear the line by running an air hose down the pipe and blowing out the debris clog.  Collection gallery orifices were backflushed every three hours around the clock to ensure they remained free of materials that might impact fish passage.

Transportation Facility:   Fish collection and transportation activities concluded on October 31.  The separator system is presently operating under the secondary bypass mode with all fish routed out through the long pipe to mid-river release.  This activity will continue until December 15 (weather permitting).  The separator complex is still being manned 24/7 due to fish being routed over the separator bars.  (No PIT-tag detection system is available at Lower Granite unless fish are diverted through the separator

Transport Summary:  All transport operations concluded on October 31.

Removable Spillway Weir:   Nothing new to report on the RSW.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Granite Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 25.0 | 15.7 | 0.0 | 0.0 | 53.0 | 50.5 | 5.0 | 5.0 |

*Cooling line intake temperature.

Other

Inline Cooling Water Strainers:   Inspection of the cooling line strainers last took place on October 14.  Two lamprey mortalities were noted.

Invasive Species:   The zebra mussel trap at the adult fishway exit was examined for zebra mussels on the October 29 inspection.  No evidence of zebra mussels was found.

Research:  The sample rate at the adult fish trap remained at 10% during the report week.  In addition, the protocol for taking scale samples from hatchery steelhead remained at one in 20 fish.  PIT-tagged Chinook are still being released back into the ladder following an operculum punch.  Transport of adult fall Chinook to Lyon’s Ferry Hatchery continued during the week.  Fish are being transported to Lyon’s Ferry when numbers warrant (approximately one load every week at this time).  The Nez Perce Hatchery at Cherry Lane met their quota for the year some time ago and no longer is transporting fall Chinook.