U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

#### FISH FACILITIES WEEKLY REPORT

#03-2011

# Project:  McNary

# Biologists: Carl Dugger and Bobby Johnson

Dates: March 11 - 17, 2011

## Turbine Operation

McNary had 10 turbine units available for power generation this week.  Turbine units 2 and 7 remain out of service for the rewind contract which likely be completed in May.  Turbine unit 10 remains out of service until March 19 in support of stator ground work and repairs.  On March 15, turbine units 13, 14 and transmission line 6 tripped during a test on a newly installed relay.  Powerhouse crews were able to restore normal operation within 10 minutes.  Turbine unit 13 returned to regular service on March 17 after relay replacement and tests were successfully completed.  The hard constraint one percent operational criteria will begin April 1.

## Adult Fish Passage Facilities

On March 13, 15 and 17, a McNary fisheries biologist performed measured inspections of the adult fishways.  Adult fish counts will resume April 1.

### Fish Ladders: Both ladders met all Fish Passage Plan criteria during measured inspections.  On March 13, biologists noted that the Oregon exit weir set points had been adjusted.  The new exit traveling screens were set to run 12 times a day for 20 minutes.  Observations confirmed on 2 occasions that these screens were running as programmed.  Traveling screen differentials were satisfactory all through the week.  The Washington ladder and exit operated smoothly without incident throughout this week.

Fishway Entrances and Collection Channel:  All Washington ladder inspection points were in criteria.  All Oregon ladder inspection points were in criteria except for the north powerhouse pool differential, the south pool differential and SFEW1.  The north powerhouse pool differential measured 0.7 to 0.9 feet.  This is probably due to the juvenile facility being out of service.  When available, excess water from the juvenile fish facility is added to the adult collection channel.  On March 15, the south pool differential measured 0.9 feet and on March 17, SFEW1 measured 8.8 feet.  These measurements maybe partly due to calibration drifts caused by hydraulic gradients created by involuntary spill.  Collection channel velocities averaged 1.6 feet per second.

Auxiliary Water Supply System:  For the week, fish pumps 1 and 3 were continuously in service with blade angles of 30 degrees.  Pump 2 remains out of service for major overhaul including upper and lower bearing replacements.  Pump 2 is expected to remain out of service until approximately mid-April.  As mentioned above, the juvenile facility is not yet supplying the usual 450 cfs to the north powerhouse pool.  The Wasco County PUD went out of service on 2 occasions this week.  The first outage lasting 2 hours took place March 15 when turbine units 13, 14 and transmission line 6 tripped out of service during relay tests (mentioned above).  The second outage lasting 1.1 hours was a planned outage in support of turbine unit 13 tests.  The bypass system functioned well during the two PUD outages.

#### Juvenile Fish Passage Facility

The facility remains shut down for winter maintenance, which is nearing completion.  On March 17, facility personnel noted heavy spalling on the floor of the juvenile channel.  About 1/16 inch of concrete cream peeled from the channel floor in a random pattern due to repetitive freezing, thawing and toughening over 17 winters.  The term “cream” refers to the smooth surface layer that is “finished” after concrete is poured.  The amount of spalling is enough to concern project personnel and will be removed early next week with fire hoses.  On approximately March 23, the facility’s emergency supply water will be opened for a day in order to check for unknown freeze breaks.  Primary bypass operations are approximately scheduled to begin March 29.  This will give the facility staff about three more days for maintenance and repairs prior to the formal start of routine primary bypass operations on April 1.  ESBS installations in operational turbine units are to begin April 5.  The first day of secondary bypass and sample collection will be April 6.  This will mark the start of the spring bypass season with alternating days of primary and secondary bypass.

Forebay Debris/Gatewell Debris/Oil:  For the week, forebay debris was light to heavy depending on flow patterns and wind direction.  Trash rack differential recordings showed measurements of 2.2 to 5.7 feet at turbine units 3, 5, 9 and 11.  Cleaning will resume on March 21.  Recovered debris will be monitored for trapped juvenile lamprey.  Trash rack differential monitoring will continue.  No problems were observed in the gatewell slots this week.

ESBSs/VBSs:  The project plans to install the screens from approximately April 4 to 14 in similar fashion as the last two seasons for juvenile lamprey passage.  April 4 ESBS installations are planned only in slots associated with turbine units 2 and 7.  These two turbine units are undergoing rewinds and not expected to return to service until May.  The installations of the remaining ESBSs will begin April 5.  When fish screen installation begins, VBS monitoring will resume.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  The orifices remain closed for winter maintenance which is nearing completion.  The channel will be re-watered and bypass operations will begin on approximately March 29.  As mentioned above, concrete spalling found on the channel floor will be removed next week.

Transportation Facility:  The facility remains dewatered for winter maintenance which is near completion.

Transport Summary:  There is no transport taking place at this time.

River Conditions

River conditions during the week are outlined in Table 1 as provided by the control room.  Data periods runs from 0000 hours to 2400 hours each day.  Spillway gate control upgrades continue.  Due to river flow in excess of powerhouse capacity, involuntary spill occurred all week.  The project plans to install the spillbay weirs before April 10.

Table 1.  River conditions at McNary Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 229.4 | 199.4 | 70.9 | 38.9 | 40 | 39 | 5.0 | 2.7 |

*Unit 1 scroll case temperature.

Other

Inline Cooling Water Strainers:  Main turbine unit cooling water strainers were examined on March 8 to 10 and 14.  A total of 57 juvenile lampreys were recovered.  The next inspection will take place in April.

Invasive Species:  A zebra mussel station examination took place March 15.  No invasive species were noted.

Bird counts will resume on March 27 when fisheries technicians begin shift work in preparation for the spring season.  An occasional gull, grebe or cormorant was observed during ladder inspections and other work.  The adult fallback study continues.  Other researchers are  preparing for the upcoming season.

Project:  Ice Harbor

# Biological Technician: Steve Jeffers

Dates: March 11 - 17, 2011

## Turbine Operation

Turbine units 2, 3, 5, and 6 were available for operation this reporting period.  Turbine unit 1 was unavailable March 14 from 0855 hours to 1536 hours due to trolley pipe installation.  Turbine unit 4 remains out of service for blade repair.

## Adult Fish Passage Facilities

### Fish facility personnel inspected the adult fishways March 14, 15, 16, and 17.

### Fish Ladders:  All north and south adult fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria. The adult collection channel velocity meter is not functioning.  A trouble report to fix the meter has been initiated and a replacement device is on the way.

### Fishway Entrances and Collection Channel (inspection date order):  The south shore entrance (SFE) was off sill with a depth of 8.1 feet, off sill with 8.1 feet, off sill with 8.1 feet, and off sill with 8.2 feet.  The north powerhouse entrance (NFE) was off sill with a depth of 8.0 feet, off sill with 8.2 feet, off sill with 8.2 feet, and off sill with 8.1 feet.  The north shore entrance (NSE) was off sill with a depth of 9.1 feet, off sill with 9.7 feet, off sill with 9.3 feet, and off sill with 11.6 feet.  Fishway entrance criterion is 8 feet depth, greater than 8 feet depth, or on sill.  All channel/tailwater differentials were in criteria.  Channel/tailwater differential criteria are 1 – 2 feet.

### Auxiliary Water Supply System:  Two of the 3 north shore fish pumps were operated without problems.  All north shore fish pumps are in service.  Five of 8 south fish pumps are in service.  South fish pump 1 is out of service due to vibrations and south fish pump 3 is out of service due to gearbox problems.  South fish pump 8 is on stand-by and is available for service.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  No problems to report.  Debris is accumulating in the forebay in front of the powerhouse.  Fish ladder exits are clear of debris and the bubblers are operating.  Turbine unit trash rack raking is scheduled for the week of March 28.

STSs/VBSs:  STSs are raised for annual maintenance. STSs are scheduled to be lowered into operating position the week of March 28.

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe:   The juvenile fish bypass is not in operation.  All orifices are closed.  Start-up is scheduled for March 24.

Juvenile Bypass Facility:  The bypass is scheduled to be put into operation March 24.

Fish Sampling:  The first sample is scheduled for April 11.  Sampling days will be Monday and Thursday through the beginning of July.

Removable Spillway Weir (RSW):  The RSW is in operation for involuntary spill.  Routine spill for fish passage will begin April 3, 2011.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Ice Harbor Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 88.4 | 43.1 | 12.5 | 0.0 | 40 | 40 | 3.6 | 3.3 |

*Unit 1 scrollcase temperature.

Inline Cooling Water Strainers:   Cooling water strainers were last inspected February 23.  A total of 21 lamprey mortalities were recovered.

Invasive Species:  A zebra mussel inspection was performed in the collection channel during winter maintenance.  None were found.

# Project:  Lower Monumental Dam

# Biologists:  William Spurgeon and Elizabeth Lindsey

Dates: March 11 - 17, 2011

## Turbine Operation

All turbine units are being operated under the soft 1% operational constraint criteria.  Turbine units 4, 5 and 6 operated outside the 1% criteria on March 12 from 0804 to 1101 hours.

Adult Fish Passage Facility

Adult fishways were inspected by Corps biologists on March 11, 14, 15, 16 and 17.

Fish Ladders: Fishway exit head differentials and depths over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively) on all inspections.  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively) on all inspections.

### Fishway Entrances and Collection Channel:  NSE1 and NSE 2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections.  North shore channel/tailwater head was in criteria (1’-2’) on all inspections.

SPE 1 and SPE 2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections.  South powerhouse channel/tailwater head was in criteria (1’-2’) on all inspections.

SSE1 weir gate was in depth criteria (criteria: > 8’ or on sill) on all inspections.  SSE 2 was in criteria (6’ above sill) on all inspections.  South shore channel/tailwater head was in criteria (1’-2’) this week.

### Auxiliary Water Supply System (AWS): All AWS pumps were in service and operating satisfactory throughout this period.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil: There was an average of 450 square yards of forebay debris observed during this period.  Debris was removed from the gatewells and trash racks during the week of March 11 through 14.

STSs/VBSs: STSs were installed on March 13 and 14.

Orifices, Collection Channel, Dewatering Structure, Flume: The bypass was watered up on March 14 at 1520 hours.

Collection Facility:  Winter maintenance is being finished up.  The facility will be watered up for testing the week of March 21.

Transport Summary:  No fish transport operations in progress at this time.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Monumental Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF)* |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 88.1 | 41.6 | 0 | 0 | 42.0 | 40.0 | 2.4 | 0.9 |

*Scrollcase temperatures.

#### Other

Inline Cooling Water Strainers:   Cooling water strainers were last inspected March 3.  Forty-three lamprey and 4 Siberian prawn were recovered.

Invasive Species:  There were no zebra mussels observed at the monitoring stations at the end of February.

Project:  Little Goose

# Biologists: George Melanson and Richard Weis

Dates: March 11 - 17, 2011

## Turbine Operation

Turbine units 1 through 6 were available for service this report period.  All turbine units were operated under the soft constraint of the 1% efficiency criteria.

## Adult Fish Passage Facility

USACE fisheries biologists performed measured inspections of the adult fishway on March 14, 16 and 17.

Fish Ladder:  All criteria were met.

Fishway Entrances and Collection Channel:  Most fishway measurements were in criteria during inspections.  Channel to tailwater head differentials ranged between 1.04 and 1.60 feet (criteria 1.0 to 2.0 ft.).  SSE weir depths ranged between 8.62 and 10.08 feet (criteria ≥8.0 ft), NPE 1 and 2 ranged between 7.12 and 7.32 feet (criteria ≥7.0 ft or on sill) and NSE weir depths ranged between 7.90 and 9.18 feet (criteria ≥ 6.0 ft.).  Collection channel water velocities (criteria 1.5 fps) ranged from 1.2 and 2.2 fps near the SSE.  Subsurface water velocities near the SSE (flowmeter) electronically reported 0.8 fps.

Auxiliary Water Supply System:  All fish pumps operated in criteria.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Up to 4,000 square feet of floating debris accumulated inside the trash-shear boom.

ESBS/VBS:  All ESBS remained raised and in their winter storage positions.  Maintenance is ongoing.

Orifices, Collection Channel, Dewatering Structure, Flume:  The juvenile collection system is out of service for winter maintenance.

Transportation Facility:  The facility is out of service for winter maintenance.

Transport Summary:  Transport operations are expected to begin in late April or early May.

Spillway Weir:  The spillway weir was not in service during this report period.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Little Goose Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 75.8 | 34.0 | 0 | 0 | 41.9 | 41.4 | 3.5 | 2.9 |

*Ladder temperature.

Other

Cooling Water Strainers:  On March 17, cooling water strainers were inspected.  Four juvenile lamprey mortalities were removed.  The next inspection is scheduled for March 23.

Invasive Species:  The Zebra Mussel substrate monitor is scheduled for inspection on April 5.

Avian Activity: A few gulls were observed this report period.

Project:  Lower Granite

# Biologists:  Mike Halter and Ches Brooks

Dates: March 11 - 17, 2011

## Turbine Operation

Lower Granite had turbine units 1, 2, 4 and 6 available for power generation at the beginning of the report week.   Turbine unit 3 remained out of service for a rewind and the estimated return to service date is now April 29, 2011.  Turbine unit 5 is out of service for stator repair and the estimated return to service date is May 13, 2011.  Validation testing was conducted during the report week.  The following outages took place in support of validation testing:  turbine unit 1 on March 15 (1042 – 1649 hours), turbine unit 2 on March 16 (0820 – 1125 hours).

## Adult Fish Passage Facility

On March 14, 15, and 16, Lower Granite fisheries biologists performed measured inspections of the adult fishway system.  Video counts in the adult fish ladder began March 1.  Recording times are from 0600 to 1600 hours.

Fish Ladder:  All criteria were met.

Fishway Entrances and Collection Channel:  Head differential readings remained within criteria at all adult fishway entrances during the weekly inspections.  Weir depths at the south shore and north powerhouse fishway entrances were also within criteria on all inspections this week due to the tailwater elevation exceeding 636.0 feet.  Weir depths at the north shore fishway entrances were out of criteria all week with readings of between 4.9 and 5.1 feet (criterion ≥ 7.0 feet).  Weir depth readings at the north shore entrances are being sacrificed in order to maintain the requisite 1.0 foot of head differential.  Velocity readings in the adult fishway collection channel transition pool area ranged from 0.93 to 1.11 feet per second and averaged 1.02 feet per second for the week.

### Auxiliary Water Supply System:  There were no problems with the auxiliary water system during this report period.

#### Juvenile Fish Passage Facility

The juvenile fish collection/bypass system has been shut down for the winter outage since December 21, 2010.  Water up of the collection gallery and the initiation of primary bypass is scheduled for the morning of March 21.  Fish screen installation activities are also scheduled to start on March 21.  Sampling activities are scheduled to begin on March 25.

Forebay Debris/Gatewell Debris/Oil:  Forebay debris was minimal and none was removed this week.

ESBSs/VBSs:  The ESBSs remain raised and “dogged-off” for maintenance work during the week.  Deployment of ESBSs is tentatively scheduled to begin on March 21.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  The juvenile fish collection gallery will be watered up on the morning of March 21 in support of fish screen deployments.

Transportation Facility:  The start of general fish transport operations are uncertain at this time but will probably commence in late April or early May due to the above average snowpack conditions.  Research barge operations are tentatively slated to begin April 7.  Juvenile fish sampling (only) activities are tentatively scheduled to begin on March 25.

Transport Summary:  Fish transport is not taking place at this time.

Removable Spillway Weir (RSW):  The RSW is not in service at this time.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Granite Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 74.6 | 48.9 | 0.0 | 0.0 | 45.6 | 43.9 | 2.2 | 1.8 |

*Scrollcase temperature.

Other

Inline Cooling Water Strainers: The last lamprey inspections were last conducted on February 24.  A total of 113 lamprey mortalities were removed from the strainers.  The next inspections are scheduled for March 30-31.

Invasive Species:  The zebra mussel trap at the adult fishway exit was replaced with a new trap using scrub pad material on March 7.  The old trap was refurbished with new net mesh material and was deployed on March 9.  Both traps will be utilized this season

Research: The adult fish trap was watered up on March 7.  The initial sample rate was set at 10%.  Scale samples are being taken from one out of every 20 hatchery steelhead.  All captured unclipped steelhead are being PIT-tagged, and scale and genetic samples are being taken from these fish.  Previously PIT-tagged steelhead (either clipped or unclipped) will have both scale and genetic samples taken for verification purposes.