U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

#### FISH FACILITIES WEEKLY REPORT

#10-2011

# Project:  McNary

# Biologists: Carl Dugger and Bobby Johnson

Dates: April 29 – May 5, 2011

## Turbine Operation

McNary had 12 units available for power generation this week.  Units 2 and 7 remain out of service for the rewind contract which should be completed by the end of May.  On May 2, units 4 through 6 were out of service a total of 1.3 hours for ESBS camera inspections.  On April 1, the hard constraint one percent criteria began with no units running outside the criterion.

## Adult Fish Passage Facilities

On May 1, 4 and 5, the McNary fisheries biologist performed measured inspections of the adult fishways.  Adult fish counting continues.

### Fish Ladders:  During measured inspections, all Fish Passage Plan criteria were met on both ladders.  At the Washington exit, the regulating weir alarmed once and was reset.  At the Oregon exit, three false traveling screen differential alarms occurred with measured readings revealing no problems.

Fishway Entrances and Collection Channel:  On the Washington ladder, all inspection points were in criteria except on May 1 and 5, when entrance weir, W3, measured 7.4 and 7.6 feet, respectively.  The weir was recalibrated again.  Heavy spill in the area of the weir maybe causing these calibration drifts.  On the Oregon ladder, all inspection points were in criteria.  The collection channel velocity average 1.5 feet per second.

Auxiliary Water Supply System:  For the week, fish pumps 1 and 3 were in service with blade angles of approximately 30 degrees no three interruptions recorded.  At fish pump 1, a cover plate pump was replaced.  Pump 2 remains out of service due to a major overhaul including the upper and lower bearing replacement along with alignment work which results in a return to service date of June 30.

The juvenile facility continues to supplying the usual 450 cfs to the north powerhouse pool.  Finally, the Wasco County PUD unit also had no interruptions in operation.

#### Juvenile Fish Passage Facility

Alternating days of primary and secondary bypass continue for the spring season with the switch occurring every morning at 0700 hours with one interruption occurring to this schedule.  On May 3, for approximately five minutes, the system was in secondary bypass with gates off for a tour demonstration.  For the report week, 336,033 smolts and 3,500 juvenile lampreys were bypassed during secondary operations.

Forebay Debris/Gatewell Debris/Oil:  For the week, forebay debris was moderate to heavy depending on flow patterns and wind direction.  Trash rack differential recordings revealed no problems and no racks were cleaned.

No problems were observed in the gatewell slots.

ESBSs/VBSs:  ESBS’s are installed at all units except units 2 and 7, which are out of service.  The ESBS’s for these units are being prepared for installation.  The screen at 9C slot remains in bypass mode.  On April 29, the two remaining spare ESBS’s were brought up from the yard to the intake deck.  ESBS camera inspection at units 4 through 6 revealed no problems.

VBS monitoring revealed two screens out of criteria.  On April 29, these screens and one other were cleaned.  During cleaning, it was noted that the screens appeared relatively clean and measuring techniques were reviewed with the staff.  No juvenile lamprey mortalities were noted in any VBS’s.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  Depending on forebay elevation, 41 to 42 orifices were used this week.  When using an orifice count below 42, orifices were closed at unit 2 which is out of service.  Two orifice blockages were observed and cleared with no harm to fish was noted.  One of these blockages occurred at 6B slot with the orifice having four previous blockages mentioned last week.  While doing ESBS camera inspections, the orifice openings in the gatewell slots were examined at units 4 through 6 with no debris observed.  On April 29, the orifice at 6A slot was found closed.  The orifice was apparently inadvertently left closed earlier in the day.  No harm to fish was noted and orifice operation was reviewed with the staff.

All system operated well in automatic mode.  On May 3, the transition screen cleaning device alarmed.  No problem was found and the alarm appeared to be a timing alarm caused by debris.  On May 5, the NMFS reassembled the trap at 6B south orifice so that orifice could be used in an emergency if the north orifice developed a problem.  Besides during primary bypass and daily checks, the channel was also monitored during VBS cleaning.

Transportation Facility:  Alternating days of primary and secondary bypass continue.  With the spring bypass season, both bypass modes return all fish are to the river.  PIT tag detection will occur in the full flow pipe during primary bypass and throughout the facility during secondary bypass.  Smolt monitoring will only occur on secondary bypass days.  The primary (A and B) PIT tag slide gates were turned off and closed as the return to river lines provide a better bypass route for PIT tagged fish.  The PIT tag equipment continues to receive weekly checks.  The secondary (C and D) PIT/bypass gates were off and open as there are no studies requiring them this year.  The sample gates were activated and functioned well.  They will be turned off or on at 0700 hours each day so they will function only during secondary bypass.

Ice block checks of the return to river lines removed one small blockage from the B line this week.

Transport Summary:  There is nothing to report.

River Conditions

River conditions during the week are outlined in Table 1 as provide by the smolt monitoring staff whose data day runs from 0700 to 0700.  Clarity was provided by the control room.  The spring spill program continues with spill approximately 40 percent of total flow.

Table 1.  River conditions at McNary Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 256.3 | 232.7 | 107.1 | 93.2 | 48.9 | 47.7 | 4.0 | 3.1 |

Other

Inline Cooling Water Strainers:  The next main unit examination is scheduled for May 17.

Invasive Species:  The zebra mussel station examination on May 4 revealed nothing.

Predatory Bird Observations:  Bird counts continue with the forebay area being checked once a day and the tailwater area being checked twice a day.  In the tailwater area, high counts were 152 gulls and five pelicans with an occasional cormorant noted.  Most birds were seen in the spill basin.  By the bypass outfalls, the high counts were six gulls and four pelicans with swing shift being most active when hazing personnel were off duty.  During the week, the APHIS employee had surgery resulting in two days without hazing.  The water cannon operated well.

In the forebay area, a high count of 107 grebes was noted with an occasional cormorant, pelican, gull, tern or osprey observed.  Two grebes join the grebe from last week for a total of three in the gatewell slots.  All three passed to the collection channel and out of the system.  Finally, pelicans and gulls continue to roost on the rocks by the Washington boat dock.

Research:  The study of the Oregon ladder exit area by the traveling screens continues.  On April 29, the fisheries staff began to assist in monitoring the debris trap at night.  Gas bubble trauma examinations and preparations for other studies also continue.

Project:  Ice Harbor

# Biologist: Mark Plummer

Technician: Stephen Jeffers

Dates: April 29 – May 5, 2011

## Turbine Operation

Turbine units 1, 2, 3, 5, and 6 were available for operation this reporting period.  Turbine unit 4 remains out of service for blade repair.

## Adult Fish Passage Facilities

### Fish facility personnel inspected the adult fishways May 2, 3, 4, and 5.

### Fish Ladders:  All north and south adult fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria. The adult collection channel velocity meter is not functioning.

### Fishway Entrances and Collection Channel (inspection date order):  The south shore entrance (SFE) was off sill with a depth of 8.3 feet, off sill with 8.1 feet, off sill with 8.5 feet, and off sill with 8.3 feet.  The north powerhouse entrance (NFE) was off sill with a depth of 9.7 feet, off sill with 8.4 feet, off sill with 9.2 feet, and off sill with 9.4 feet.  The north shore entrance (NSE) was off sill with a depth of 9.2 feet, off sill with 8.1 feet, off sill with 9.8 feet, and off sill with 9.5 feet.  Fishway entrance criterion is 8 feet depth, greater than 8 feet depth, or on sill.  All channel/tailwater differentials were in criteria.  Channel/tailwater differential criteria are 1 – 2 feet.

### Auxiliary Water Supply System:  2 of the 3 north shore fish pumps were operated without problems.  All 3 north shore fish pumps are operational.  6 of 8 south fish pumps are in service and operating. South fish pumps 1 and 3 are out of service due to vibration problems.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  No problems to report.  The forebay is clear of debris.  Debris is passing the dam due to spill.  Fish ladder exits are clear of debris and the bubblers are operating.

STSs/VBSs:  The STS’ are in cycle run timing mode.  No problems were found during the April STS video inspection.  May STS video inspection is scheduled for May 24.

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe:   The juvenile fish bypass is in operation.  20 orifices are open.

Juvenile Bypass Facility:  The bypass was put into operation March 23.

Fish Sampling:  Juvenile fish sample days are Monday and Thursday through the beginning of July.

Removable Spillway Weir:  The RSW is in operation.

Fish Sampling:

May 2:

| Species | Sampled | #Descaled | Morts | Avian Marks |
| --- | --- | --- | --- | --- |
| C-CH | 61 | 2 | 0 | 0 |
| UC-CH | 56 | 3 | 0 | 0 |
| C-CH-O | --- | --- | --- | --- |
| UC-CH-O | --- | --- | --- | --- |
| C-SH | 32 | 0 | 0 | 0 |
| UC-SH | 3 | 1 | 0 | 0 |
| C-COHO | --- | --- | --- | --- |
| UC-COHO | 1 | 0 | 0 | 0 |
| C-SOCK | --- | --- | --- | --- |
| UC-SOCK | 4 | 0 | 0 | 0 |
| TOTAL | 157 | 6 | 0 | 1 |

May 5:

| Species | Sampled | #Descaled | Morts | Avian Marks |
| --- | --- | --- | --- | --- |
| C-CH | 61 | 2 | 0 | 0 |
| UC-CH | 54 | 2 | 0 | 1 |
| C-CH-O | --- | --- | --- | --- |
| UC-CH-O | --- | --- | --- | --- |
| C-SH | 31 | 0 | 0 | 1 |
| UC-SH | 4 | 0 | 0 | 0 |
| C-COHO | --- | --- | --- | --- |
| UC-COHO | --- | --- | --- | --- |
| C-SOCK | --- | --- | --- | --- |
| UC-SOCK | 7 | 0 | 0 | 0 |
| TOTAL | 157 | 4 | 0 | 2 |

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Ice Harbor Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 93.3 | 84.1 | 61.5 | 27.1 | 50 | 49 | 3.2 | 2.4 |

*Unit 1 scrollcase temperature.

Other

Inline Cooling Water Strainers:   Cooling water strainers were inspected April 19.  A total of 128 juvenile lamprey and 1 adult lamprey mortalities were recovered.  The adult lamprey was recovered from turbine unit 1.  Two juvenile steelhead were also recovered.

Invasive Species:  No zebra mussels were observed during this report period.

Spill for fish begin April 3, 2011.

# Project:  Lower Monumental Dam

# Biologists:  William Spurgeon and Elizabeth Lindsey

Dates: April 29 – May 5, 2011

## Turbine Operation

The units are being operated in hard constraint of the 1% operation criteria.  Units were rotated out of service on May 2 and 3 for inspection of STS screens.

Adult Fish Passage Facility

The adult fishway was inspected by Corps and PSMFC biologists on April 29, 30, May 1, and 4.

Fish Ladders: Fishway exit head differentials and depths over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively) on all inspections.  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively) on all inspections.

### Fishway Entrances and Collection Channel:  NSE 1 and NSE 2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections.  North shore channel/tailwater head was in criteria (1’-2’) on all inspections.

SPE 1 and SPE 2 weir gates were in sill criteria (criteria: > 8’ or on sill) on all inspections.  While on sill, the gate depth readings were 7.6’, 7.9’, 7.8’, and 7.5 feet.  South powerhouse channel/tailwater head was in criteria (1’-2’) on all inspections.

SSE1 weir gate was in depth criteria (criteria: > 8’ or on sill) on all inspections.  SSE 2 was in criteria (6’ above sill) on all inspections.  South shore channel/tailwater head was in criteria (1’-2’) this week.

### Auxiliary Water Supply System: All AWS pumps were in service and operating throughout this period.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 8.3 square yards of forebay debris observed during this period.  Gatewell debris ranged from 0-20% surface coverage.  No oil was observed in gatewells.

STSs/VBSs:  STSs are operating in cycle mode.  STS inspections were conducted May 2 and 3 with all screens found in good operating condition.

Orifices, Collection Channel, Dewatering Structure, Flume:  The collection channel is operating with 20 orifices open.

Collection Facility:  Fish collection for condition monitoring began on April 1.  The final collection for condition monitoring was May 4.  Collection for species composition will begin at 1500 hours on May 6 in secondary bypass operation until 0700 hours on May 8.  Collection into the raceways for transport will begin at 0700 hour on May 8.

Transport Summary:  Not collecting for transport.  Every-day barging is scheduled to begin on May 9.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Monumental Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF)* |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 90.9 | 81.1 | 29.9 | 29.6 | 50.0 | 48.0 | 3.2 | 2.1 |

*Scrollcase temperatures.

#### Other

Inline Cooling Water Strainers: Cooling water strainers were inspected on May 3.  One live lamprey was recovered.  Mortalities included 59 lamprey, 107 salmon smolts, 26 juvenile steelhead, 1 unknown fish, and 5 Siberian prawns.

Invasive Species: There were no zebra mussels observed at the monitoring stations on April 24.

Project:  Little Goose

# Biologists: George Melanson and Rick Weis

Dates: April 29 – May 5, 2011

## Turbine Operation

Turbine units 1 through 6 were available for service this report period.  For the most part, all turbine units were operated within 1% of best efficiency.  On May 4, turbine unit one operated outside the 1% criteria from 1411 to 1436 hours.

## Adult Fish Passage Facility

COE and ODFW fisheries biologists performed measured inspections of the adult fishway April 29, May 1 and May 2.

Fish Ladder:  The ladder exit head differentials ranged between 0.1 and 0.2 feet (criteria < 0.5 ft.).  Water depths over the weirs measured 1.1 feet on all three inspections (criteria 1.0-1.3 ft.) and picketed lead head differentials held steady a 0 feet (criteria < 0.3 ft.).  No debris was observed at the picketed leads or the ladder exit.  The air bubbler used to prevent debris from collecting near the ladder exit operated satisfactorily.

Fishway Entrances and Collection Channel:  Channel to tailwater head differentials ranged between 1.64 and 1.98 feet (criteria 1.0 to 2.0 ft.).  SSE weir depths ranged between 8.32 and 8.38 feet (criteria ≥8.0 ft), NPE weirs rested on sill and depths ranged between 5.56 and 5.80 feet (criteria ≥7.0 ft or on sill) and NSE weirs remain at fixed elevations of 531.5 feet and depths ranged between 5.84 and 5.92 feet (criteria ≥ 6.0 ft.).  Collection channel surface water velocities (criteria 1.5 fps) ranged from 1.3 to 2.0 fps near the SSE and ranged from 2.3 to 2.6 fps near the NSE.

Auxiliary Water Supply System:  All fish pumps operated in criteria.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Approximately 200 to 300 square feet of floating debris was accumulated inside the trash-shear boom and positioned in front of turbine unit 1A intake.  Small amounts of debris were removed from gatewells.

Spillway Weir:  The spillway weir is operating in the low crest position.

ESBS/VBS:  All ESBS operated within criteria this report period.   Drawdown measurements across trash racks and ESBS/VBS in turbine slots 1A – 3C and 5A – 5C were performed on May 4th.  All measurements were within criteria.

Orifices, Collection Channel, Dewatering Structure, Flume:  The juvenile collection system operated in criteria with 21 open orifices.

Transportation Facility:  The juvenile fish facility switched from primary bypass operations to secondary bypass operations on April 28 at 0700 to 0700 hours the following day. The purpose of secondary bypass was to perform 24 hour fish condition sampling.  During secondary bypass an estimated 51,103 fish were collected and all were bypassed back to the river.  Condition sampling showed descaling rate at 0.4% and a mortality rate less than 0.1%.  On May 5 at 0700 hours, the facility switched from primary bypass operations to collection for transport.

Transport Summary:  Direct loading of fish onto barges commenced on May 5 at 0700 hours.  Daily barging operations at Little Goose start with the first barge departing on May 6.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Little Goose Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 88.3 | 79.9 | 26.5 | 23.9 | 49.8 | 49.2 | 2.8 | 2.8 |

*Ladder temperature.

Other

Inline Cooling Water Strainers:  On May 3, cooling water strainers were inspected.  Six salmonid smolts and 1 juvenile lamprey were removed.  All fish recovered were mortalities.

Invasive Species:  The Zebra Mussel substrate monitor was inspected on May 1.  No mussels were observed.  The next inspection is scheduled for June 1.

Avian Activity: Up to 15 gulls were observed this report period.   USDA- APHIS bird hazing continues.

Project:  Lower Granite

# Biologists:  Mike Halter and Ches Brooks

Dates: April 29 – May 5, 2011

## Turbine Operation

Lower Granite had turbine units 1, 2, 4 and 6 available for power generation at the beginning of the report week.   Turbine unit 3 remained out of service for a rewind and the estimated return to service date is now May 23, 2011.  Turbine unit 5 was out of service for stator repair early in the week and was operationally tested beginning the afternoon of May 4.  If all goes well, it will be brought back into service during the next report week.

## Adult Fish Passage Facility

On April 30, May 1, 2 and 4 the Lower Granite fisheries biologists performed measured inspections of the adult fishway system.

Fish Ladder:  All criteria were met.

Fishway Entrances and Collection Channel:  Head differential readings remained within criteria at all adult fishway entrances during the weekly inspections.  Weir depths at the south shore fishway entrances were also within criteria on all inspections this week (criterion ≥ 8.0 feet).  Both north powerhouse fishway entrances were on sill during the week due to tailwater elevations below 636.0 feet (these gates bottom out at elevations below 636.0 feet).  North powerhouse fishway entrance weir depths ranged from 5.7 to 6.4 feet. Weir depths at the north shore fishway entrances were out of criteria all week with readings of between 5.0 and 5.1 feet on both gates (criterion ≥ 7.0 feet).  Weir depth readings at the north shore entrances are being sacrificed in order to maintain the requisite 1.0 foot of head differential.  Velocity readings in the adult fishway collection channel transition pool area ranged from 0.88 to 1.13 feet per second and averaged 1.01 feet per second.

### Auxiliary Water Supply System:  There were no problems with the auxiliary water system during the report week.   Fish pump one was brought on line at 1548 hours on May 3 and fish pump three was taken off line.  Fish pumps two and three were run during the report week until the above time.

#### Juvenile Fish Passage Facility

The juvenile fish facility sample rate remained at 0.5% during the report week.

Forebay Debris/Gatewell Debris/Oil:  The amount of forebay debris varied during the week due to wind strength and direction; none was removed.

ESBSs/VBSs:  VBS/ESBS video inspections last took place on April 22.  The inspector noted that a four foot section of strapping used for securing the mesh was possibly missing from unit 2 VBS, but that poor visibility made it hard to be sure.  He also noted that the mesh was entirely in place.  This section will be checked when visibility allows.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  There were no problems with any of these structures during the week.  Orifices are being backflushed every three hours around the clock to ensure they remain free of materials that might impact fish passage.

Transportation Facility:  General transport operations began with juvenile fish collection into raceways on May 1 at 0700 hours.  Everyday barging from Lower Granite commenced the next day.  Direct loading operations began at Little Goose on May 5 with the first loaded barge scheduled to depart on May 6.

Transport Summary:  The first regular fish barge of the season departed Lower Granite on May 2.  Research fish will be barged weekly along with the regular fish collection.

Removable Spillway Weir:  The RSW operated normally as part of the spill plan.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Granite Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 92.0 | 84.8 | 20.2 | 20.1 | 52.7 | 51.1 | 3.4 | 2.5 |

*Scrollcase temperature.

Other

Inline Cooling Water Strainers:  Lamprey inspections were last conducted on April 25-26.  A total of 107 lamprey mortalities were removed from the strainers.

Invasive Species:  The zebra mussel traps near the adult fishway exit were examined for zebra mussels on the May 4 inspection.  No evidence of zebra mussels was found.

Research:  Adult fish trap operations continued with a sample rate of 10%.  Scale samples are being taken from one out of every 20 hatchery steelhead.  All wild steelhead captured are being PIT-tagged and scale and genetic samples taken.  Any previously PIT-tagged steelhead (either hatchery or wild) will have both scale and genetic samples taken for verification purposes.

NOAA-Fisheries continued tagging juvenile fish for the transport study, survival study, and extra mortality study during the week.   The goal of the survival and transport studies is to compare smolt to adult returns of in-river migrating smolts to the smolt to adult returns of transported smolts.  The goal of the extra mortality study is to determine whether migration through Snake River dams and reservoirs causes latent mortality in Snake River yearling chinook.  Two groups of hatchery-reared yearling chinook smolts are being PIT-tagged at Lower Granite.  One group is being transported by truck to below Ice Harbor Dam and released there.  A second group is being trucked an identical amount of time and then released into the tailrace below Lower Granite Dam.

Idaho Department of Fish and Game (IDFG) personnel conducted genetic stock identification work on chinook and steelhead smolts from the lab during the week.  The goal of the study is to enumerate and characterize the natural production of yearling spring/summer chinook salmon and steelhead above Lower Granite with regard to age composition and genetic stock identification.  IDFG will sample every day until the first part of July with a goal of collecting between 2000 and 4000 genetic samples each from yearling spring/summer chinook and steelhead and 500-1500 genetic samples from subyearling fall Chinook.

The Nez Perce Tribal Fisheries in coordination with the Corps and The University of Idaho started steelhead kelt research work for this season on April 10 at the holding tanks upstream of the main fish facility.   Clipped and unclipped kelts are being examined to determine the changes that occur during sexual maturity and to determine post spawning changes associated with successful downstream migration and recovery to spawn again.  In the near future, dependent on the group, steelhead kelts will be blood sampled, PIT-tagged, acoustic-tagged, trucked, barged, or returned back to the river.