U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

#### FISH FACILITIES WEEKLY REPORT

#16 - 2011

# Project:  McNary

# Biologists: Carl Dugger and Bobby Johnson

Dates: June 10 - 16, 2011

## Turbine Operation

McNary had 12 to 14 units available for power generation this week.  Following tests and final unit adjustments on June 16, unit 2 returned to service from the rewind contact though testing continues.  On June 11, units 10 through 14 were out of service a total of 4.4 hours for trash rack cleaning.  On June 13, unit 4 was out of service four minutes to “burp” the trash off the racks.  On June 14, units 13 and 14 were out of service a total of 1.2 hours for ESBS camera inspections.  From June 14 to 15, unit 7 was out of service for “hi pot” testing and ground work.  “Hi pot” or high voltage testing is a “pass/fail” test for electrical insulation.

The hard constraint one percent criterion continues with no units running outside the criteria except for unit 2 during brief periods of testing.

## Adult Fish Passage Facilities

On June 10, 12 and 14, the McNary fisheries biologist performed measured inspections of the adult fishways.  Adult fish counts continues.  On June 14, water temperature monitoring at the exits began.  On June 13, programming of Oregon entrance weirs NFEW2, NFEW3, SFEW1 and SFEW2 for adult lamprey passage was completed.  Beginning June 15, the weirs will be lowered nightly from 2100 to 0400 hours.  On Primary bypass nights, fisheries technicians will monitor the entrances to verify that the weirs are lowering.

Fish Ladders:  During measured inspections, all Fish Passage Plan criteria were met on both ladders.  By June 12, on the Washington ladder, issues with weir 334 were resolved returning the exit to normal automatic operation.

Heavy incoming debris along the Washington shore line remains an issue.  Flushing the debris down the navigation lock has helped but the debris continues to come in from upriver.  The Washington ladder picketed leads have been constantly monitored by all personnel and were repeatedly cleaned.  Also, every night of the week, the leads were raised from approximately 2100 to 0500 hours to help avoid possible flooding of the count station.  The project has scheduled the leads to be raised nightly until the debris dissipates.  Finally, the electrical staff installed lighting in the picketed lead area to improve working conditions at night.

### At the Oregon exit, on June 12, the south traveling screen was found in bypass mode.  There was no evident reason for this so the screen was immediately returned to automatic operation.  However, the south screen did have false differential alarms all week.  The technical staff is looking into the issue but calibration of the differential sensors is difficult due to the orientation of the walkway grating after the traveling screens were installed this winter.  Measured differential readings revealed no problems.

Fishway Entrances and Collection Channel:  For the week, on the Washington ladder, entrance weir, W2, measured 6.7 to 7.3 feet.  On June 10 and 12, W3 weir depths measured 7.4 and 7.8 feet, respectively.  On June 10 and 12, at the south powerhouse entrances, SFEW1 and SFEW2, the measurements ranged from 8.4 to 8.7 feet.  The south pool differential measured 0.9 feet all week.  All other inspection points were in criteria.  High flows along with high tailwater elevations, spill turbulence and hydraulic gradients maybe causing these calibration issues which can be difficult to resolve though the technical staff continues working on them.  The collection channel velocity, which is also effect by high tailwater elevations, averaged 1.0 feet per second.

Auxiliary Water Supply System:  For the week, fish pumps 1 and 3 were in service with blade angles of approximately 30 degrees with two interruptions in service on June 13 for a total of 45 minutes for a line and bus switching.  Pump 2 remains out of service due to a major overhaul.  The project now estimates the return to service date to be in January, 2012.

The juvenile facility continues to supplying the usual 450 cfs to the north powerhouse pool with no interruptions.  Finally, the Wasco County PUD unit was out of service from approximately 0000 to 0500 every night of the week due to BPA not requiring the power production.  Also, the unit was out of service on June 15 for 52 minutes with no reason recorded.  During the outage, the bypass system operated well.

#### Juvenile Fish Passage Facility

Alternating days of primary and secondary bypass continue for the spring season with the switch occurring every morning at 0700 hours two interruptions occurring to this schedule.  On June 12, from 1000 to 1010 hours, the system was switched into and out of secondary bypass twice with all gates off for technician training.  On June 13, the start of secondary bypass was delayed 45 minutes due to a possible power outage at the facility related to unit 2 testing on transmission line 1.  Later that day, a 12 minute power outage did occur with the sample gates being turned off for 37 minutes as the system remained in secondary bypass during the outage.  For the report week, 59,172 smolts and 15,100 juvenile lampreys were bypassed during secondary operations.

Forebay Debris/Gatewell Debris/Oil:  For the week, forebay debris remained light.  However, debris continues coming into the project and needs constant monitoring especially along the Washington shore.  Though trash rack differential monitoring revealed no significant problem, on June 11, the racks at units 2, 7 and 10 through 14 were cleaned removing 9.3 ten-yard truck loads of debris.  No debris was found at units 2 and 7.  This completed the trash rack cleaning which was started last week.  On June 13, unit 4 was briefly removed form service in order to “burp” debris off that unit’s racks.  No problems were observed in the gatewell slots.

ESBSs/VBSs:  ESBSs are installed at all units.  Rehabilitation continues on the two spare ESBSs.  The screens at 3B, 5C and 9C slots remain in bypass mode.  On June 14 and 16, during unit testing, the screens at 2B and 2A slots, respectively, were switched to bypass mode after alarming.  ESBS camera inspections at unit 13 and 14 revealed no problems.

VBS monitoring revealed four screens out of criteria.  On June 10, 11, and 15, these screens and 24 others were cleaned.  The project has 10 to 12 VBS’s scheduled for rehabilitation and replacement this year.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  Forty two orifices were used this week with no blockages observed.

All system operated well in automatic mode.  Besides during primary bypass and daily checks, the channel was also monitored during VBS and trash cleaning.

Transportation Facility:  Alternating days of primary and secondary bypass continue.  With the spring bypass season, both bypass modes return all fish are to the river.  PIT tag detection will occur in the full flow pipe during primary bypass and throughout the facility during secondary bypass.  Smolt monitoring will only occur on secondary bypass days.  The primary (A and B) PIT tag slide gates were turned off and closed as the return to river lines provide a better bypass route for PIT tagged fish.  The PIT tag equipment continues to receive weekly checks.  The secondary (C and D) PIT/bypass gates were off and open as there are no studies requiring them this year.  The sample gates were activated and functioned well.  They will be turned off or on at 0700 hours each day so they will function only during secondary bypass.  The only interrupts in facility operation are mention above.

Ice block checks of the return to river lines removed no blockages.  However, due to high tailwater elevations it is every difficult to see anything exit the secondary bypass line.

Transport Summary:  Fish transport is not in progress at this time.

River Conditions

River conditions during the week are outlined in Table 1 as provide by the smolt monitoring staff whose data day runs from 0700 to 0700 hours.  Clarity data was provided by the control room.  The spring spill program continues through June 19 with spill ranging from 65 to 70 percent of total flow due to high discharge in excess of powerhouse capacity.

On June 13, bay 20 returned to service with completion of TSW removal.  Work on spill gate 1, which remains out of service with the bay closed, has begun.

On June 14, the smolt monitoring staff completed deployment of their temperature probes with the first report date being June 15.  The smolt monitoring staff will record their results in a separate report.

Table 1.  River conditions at McNary Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 500.3 | 481.7 | 348.2 | 316.6 | 55.6 | 55.1 | 2.8 | 1.7 |

Other

Inline Cooling Water Strainers:  The next examination is scheduled for June 21.

Invasive Species:  The next zebra mussel station examination will occur in early July.

Predatory Bird Observations:  Bird counts continue with the forebay area being checked once a day and the tailwater area being checked twice a day.  In the tailwater area, high counts were 14 gulls and three pelicans with an occasional cormorant or tern noted.  Most birds were seen in the spill basin.  By the bypass outfalls, the high counts were four gulls and ten pelicans with an occasional tern seen.  Swing shift was the most active when hazing personnel were off duty.  Pelicans were also observed by the adult return outfall.  The water cannon operated well.

In the forebay area, a high counts were 65 grebes and two terns with an occasional pelican, night heron or osprey observed.  The 27 grebes already in the gatewell slots were join by 12 others for a total of 39 birds.  Seven of these birds passed to the collection channel leaving 32 grebes in the gatewell slots by week’s end.  On June 15 and 16, the project netted 28 birds from the gatewell slots which left only four grebes in the slots.  All seven grebes that arrived in the collection channel passed out of the system with one being removed from the separator.  Large numbers of birds, mostly pelicans, are also roosting on the rocks by the Washington boat dock.

Research:  The study of the Oregon ladder exit area by the traveling screens continues with the fisheries staff assisting in monitoring the debris trap at night when primary bypass is occurring.  The debris trap is no currently in use during secondary bypass nights due to the in river debris loads.  Preparations for the adult lamprey passage study are also on going.  Gas bubble trauma examinations continue and results can be requested from the smolt monitoring staff.  The ODFW angling survey for small mouth bass in the project’s tailwater and forebay adjacent to the powerhouse also continues.  Finally, CRITFC will install cameras in the A side PIT tag system to monitor tagged fish next week.

Project:  Ice Harbor

Biologist: Mark Plummer

Biological Technician: Stephen Jeffers

Dates: June 10 - 16, 2011

## Turbine Operation

Turbine units 1, 2, 3, 4, 5, and 6 were available for operation this reporting period.

## Adult Fish Passage Facilities

### Fish facility personnel inspected the adult fishways June 13, 14, 15, and 16.

### Fish Ladders:  All north and south adult fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria. The adult collection channel velocity meter is not functioning.   Installation of the new equipment cannot be completed until the adult south fish ladder is unwatered this winter maintenance period.

### Fishway Entrances and Collection Channel (inspection date order):  The south shore entrance (SFE) was off sill with a depth of 8.7 feet, off sill with 8.9 feet, off sill with 9.8 feet, and off sill with 9.8 feet.  The north powerhouse entrance (NFE) was off sill with a depth of 8.5 feet, off sill with 10.4 feet, off sill with 9.4 feet, and off sill with 9.4 feet.  The north shore entrance (NSE) was off sill with a depth of 10.1 feet, off sill with 9.6 feet, off sill with 10.1 feet, and off sill with 9.1 feet.  Fishway entrance criterion is 8 feet depth, greater than 8 feet depth, or on sill.  All channel/tailwater differentials were in criteria, except June 16.  On this inspection, the north channel/tailwater differential was 0.5 feet due to the adult fish entrance weir lifting mechanism failing.  The adult entrance weir later fell to sill which restored the depth criteria.  High river flows are maintaining adult passage criteria at this entrance.  Plans are to repair the entrance hoisting mechanism when the water flows reduce.  Channel/tailwater differential criteria are 1 – 2 feet.  Repairs will be made when river flows lower and access to the entrance weir can be accomplished.

### Auxiliary Water Supply System:  Normally, 2 of the 3 north shore fish pumps are operated.  All north shore fish pumps were available for operation.  No problems were observed with the north shore fish pumps.  South shore fish pump 1 remains out of service due to vibration issues at the gearbox shaft.  All south shore fish pumps were shut down June 13 from 1211 hours to 1501 hours to reduce the head on the center powerhouse fish entrance to allow lifting of the weir for unscheduled maintenance.  Six of 7 available south shore fish pumps are operating.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  No problems to report.  Debris is accumulating in the forebay.  Fish ladder exits are clear of debris and the bubblers are operating.

STSs/VBSs:  STS rotations are in continuous run mode as the average length of both subyearling Chinook and migratory sockeye are below 120 mm.  The May 31 video inspection was not performed due as the turbidity of the water prevented viewing.  The next STS video inspection is scheduled for June 21.

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe:   The juvenile fish bypass is in operation.  Twenty orifices are open.

Juvenile Bypass Facility:  The bypass was put into operation March 23.

Removable Spillway Weir:  The RSW is in operation.

Fish Sampling:  Juvenile fish sample days are Monday and Thursday through the beginning of July.  Current sampling results are included in the tables below.

June 13:

| Species | Sampled | #Descaled | Morts | Avian Marks |
| --- | --- | --- | --- | --- |
| C-CH | 2 | 0 | 0 | 0 |
| UC-CH | 1 | 0 | 0 | 0 |
| C-CH-O | 66 | 0 | 0 | 0 |
| UC-CH-O | 72 | 0 | 0 | 0 |
| C-SH | 1 | 0 | 0 | 0 |
| UC-SH | 4 | 2 | 0 | 3 |
| C-COHO | --- | --- | --- | --- |
| UC-COHO | --- | --- | --- | --- |
| C-SOCK | 1 | 0 | 0 | 0 |
| UC-SOCK | --- | --- | --- | --- |
| TOTAL | 147 | 2 | 0 | 3 |

June 16:

| Species | Sampled | #Descaled | Morts | Avian Marks |
| --- | --- | --- | --- | --- |
| C-CH | 2 | 0 | 0 | 0 |
| UC-CH | 2 | 0 | 0 | 0 |
| C-CH-O | 52 | 0 | 0 | 0 |
| UC-CH-O | 45 | 1 | 0 | 0 |
| C-SH | 5 | 0 | 0 | 1 |
| UC-SH | 13 | 2 | 0 | 0 |
| C-COHO | --- | --- | --- | --- |
| UC-COHO | --- | --- | --- | --- |
| C-SOCK | --- | --- | --- | --- |
| UC-SOCK | 1 | 0 | 0 | 0 |
| TOTAL | 120 | 3 | 0 | 0 |

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Ice Harbor Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 202.9 | 181.6 | 122.1 | 99.0 | 55 | 55 | 2.2 | 2.2 |

*Unit 1 scrollcase temperature.

Other

Inline Cooling Water Strainers: The turbine unit 3 strainer was inspected May 31.  No lamprey or fish were found.

Invasive Species: No zebra mussels were observed during this period.

Spill for fish begin April 3, 2011.

# Project:  Lower Monumental Dam

# Biologists:  William Spurgeon and Elizabeth Lindsey

Dates: June 10 - 16, 2011

## Turbine Operation

The units are being operated in hard constraint of the 1% operation criteria.

Adult Fish Passage Facility

The adult fishway was inspected by Corps and PSMFC biologists on June 10, 11, 13, and 15.

Fish Ladders: Fishway exit head differentials and depths over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively) on all inspections.  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively) on all inspections.

### Fishway Entrances and Collection Channel:  NSE 1 and NSE 2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections.  North shore channel/tailwater head was in criteria (1’-2’) on all inspections.

SPE 1 and SPE 2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections with the exception of SPE 1 weir gate having a depth reading of 7.2 feet on June 15.  The powerhouse operator was immediately notified the gate was out of criteria and electricians made adjustments to correct the problem that day.  South powerhouse channel/tailwater head was in criteria (1’-2’) on all inspections.

SSE1 weir gate was in depth criteria (criteria: > 8’ or on sill) on all inspections.  SSE 2 was in criteria (6’ above sill) on all inspections.  South shore channel/tailwater head was in criteria (1’-2’) this week.

### Auxiliary Water Supply System:  All AWS pumps were in service and operating throughout this period.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 589.4 square yards of forebay debris observed during this period.  Gatewell debris ranged from 0 - 70% surface coverage.  The 70% reading was taken on June 10 in gatewell 2C.  Gatewell debris was removed on June 11.  No oil was observed in gatewells.

STSs/VBSs: STS operation remained in continuous run mode as average fork length of sub-yearling chinook and/or sockeye is less than 120mm.  STS inspections were conducted June 6 and 7 with all screens found in good operating condition.

Orifices, Collection Channel, Dewatering Structure, Flume:  The collection channel is operating with 20 orifices open.  The primary dewatering structure mechanical screen cleaner remains out of service due to an undetermined problem.  A trouble report has been submitted.  The pneumatic screen cleaner has been set to cycle every 10 minutes and is more than adequate for removing debris from the screen.

Collection Facility:  All fish in raceways were bypassed to the river on June 10 due to high river flow creating unsafe transit conditions.   Collection for transport was not interrupted.  Both A and B side PIT-tag gates were out of service on June 10 from 2000 hours to 2100 hours to remove debris from one of the B side counter tunnels.  On June 12 it was noticed that the supply flow for raceway 4 had diminished.  This required cleaning of the raceway 4 diffuser screens on June 15.  No fish were loaded into raceway 4 during this period.

Transport Summary:  Alternate day transport is occurring with barges arriving on even numbered days.  Barging operations were canceled on June 10 due to the high river flows creating unsafe barge transit across the river as determined by the towboat captain.  Barging resumed as scheduled on June 12.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Monumental Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF)* |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 199.5 | 177.2 | 84.8 | 60.2 | 55.0 | 53.5 | 1.5 | 1.5 |

*Scrollcase temperatures.

#### Other

Inline Cooling Water Strainers: Cooling water strainers were inspected on June 1.  No live lamprey were recovered.  Mortalities included 2 lamprey, 27 salmon smolts, 17 juvenile steelhead, 0 Siberian prawns and no unknown other fish.

Invasive Species: There were no zebra mussels observed at the monitoring stations on June 5.

Pelican presence at the bypass outfall pipe has remained low this week.  These birds are being hazed when present.

Project:  Little Goose

# Biologist: Richard Weis

Dates: June 10 - 16, 2011

## Turbine Operation

Turbine units 1 through 5 were available for service.  Turbine unit 6 remained out of service due to transformer bushing issues.  Operating turbine units were within 1% of best efficiency.

## Adult Fish Passage Facility

COE and ODFW fisheries biologists performed measured inspections of the adult fishway June 10, 14, and 15.

Fish Ladder:  The ladder exit head differentials ranged between 0 and 0.1 feet on all three inspections (criteria < 0.5 ft.).  Water depths over the weirs ranged between 1.0 and 1.1 feet (criteria 1.0-1.3 ft.) and picketed lead head differentials held steady a 0 feet (criteria < 0.3 ft.).  No debris was observed at the picketed leads or the ladder exit.  The air bubbler used to prevent debris from collecting near the ladder exit operated satisfactorily.

Fishway Entrances and Collection Channel:  Channel to tailwater head differentials ranged between 1.14 and 1.96 feet (criteria 1.0 to 2.0 ft.).  SSE weir depths ranged between 8.16 and 8.36 feet (criteria ≥8.0 ft), NPE weirs ranged between 7.04 (sill) and 7.18 feet (criteria ≥7.0 ft or on sill) and NSE weirs remain at fixed elevations of 531.5 feet and depths ranged between 6.60 and 7.76 feet (criteria ≥ 6.0 ft.).  Collection channel surface water velocities (criteria 1.5 fps) ranged from 1.8 to 2.6 fps near the SSE.  NSE was not recorded this week due to closure of North shore area from spill damage.

Auxiliary Water Supply System:  All fish pumps operated in criteria.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:   Up to 1600 sq. ft. of debris was seen in the forebay.  Small amounts of debris were removed from gatewells.  Up to 8,000 sq. is in front of the spillway.

Spillway Weir:  The spillway weir is operating in the low crest position.

ESBS/VBS:  All ESBS operated within criteria this report period.

Orifices, Collection Channel, Dewatering Structure, Flume:  The juvenile collection system operated in criteria with 21 open orifices.

Transportation Facility:  Collection for this period ranged between 15,324 and 27,827 for a total of 162,000 for the week.  All fish were transported except for mortalities.  Descaling and mortality rates for this report period are 0.2% and < 0.8% respectively.

Transport Summary:  Every other day barging operations were successfully performed this report period.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Little Goose Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 188.6 | 169.0 | 98.7 | 78.8 | 55.0 | 53.2 | 1.8 | 1.5 |

*Ladder temperature.

Other

Inline Cooling Water Strainers:  Cooling water strainers on all units were inspected during this period. 2 Lamprey and 1 Salmonid were found.

Invasive Species:  The zebra mussel substrate monitor was inspected on June 2.  No mussels were observed.  The next inspection is scheduled for July 1.

Avian Activity: Up to 5 gulls were observed this report period.   USDA- APHIS bird hazing continues and has been extended until June 22 to make up lost days at the beginning of the season.

Project:  Lower Granite

# Biologists:  Mike Halter and Ches Brooks

Dates: June 10 - 16, 2011

## Turbine Operation

Lower Granite had turbine units 1 - 6 available for power generation at the beginning of the report week.   Turbine unit #1 was taken out of service between 1054 and 1301 hours on June 12 due to a flooded guide bearing (and the need to change the oil).  All operating units were run within the operational guidelines.

## Adult Fish Passage Facility

On June 10, 11, 13 and 15 the Lower Granite COE fisheries biologists performed measured inspections of the adult fishway system.

Fish Ladder:  All criteria were met with the exception of the diffuser 14 reading which remained between 727.9 and 727.8 feet on all inspections (0.1 – 0.2 feet below criteria).

Fishway Entrances and Collection Channel:  Problems developed with the weir motor and cable control system on north shore fishway entrance number 1 (NSE-1) on the morning of May 31.  Inspection revealed that the cable had broken and the weir gate had dropped to the sill.  The weir motor was also burned up.  A temporary adjustment was done on the weir gate by crane on June 7 and the gate was dogged off at 635.0 feet by cables.  This setting will be maintained until an A-frame and chain hoist system can be put in place to adjust the weir depth relative to the tailwater elevation.  Head differential readings are supposed to remain within 1.0 to 2.0 feet at all fishway entrances.   Head differential readings were within criteria with the exception of the June 10 inspection in which the north shore fishway entrance was slightly above the criteria level with a reading of 2.1 feet.  Weir depths at the south shore and north powerhouse fishway entrances remained within criteria on all inspections this week. Weir depths at the north shore fishway entrances were out of criteria on all inspections this week.  The readings on NSE-1 were off the scale (due to the temporary cable fix) while the readings on NSE-2 ranged from 5.2 to 6.8 feet (criteria ≥ 7.0 feet).  Velocity readings in the adult fishway collection channel transition pool area ranged from 0.89 to 1.04 feet per second and averaged 0.96 feet per second.

### Auxiliary Water Supply System:  There were no problems with the auxiliary water system during the report week.   Fish pumps one and two were run all week.

#### Juvenile Fish Passage Facility

The juvenile fish facility sample rate was increased from 2.0% to 4.0% at 0700 hours on June 16 and remained at that level through the duration of the report week.

Forebay Debris/Gatewell Debris/Oil:  The amount of forebay debris varied during the week due to wind strength and direction.  A forebay debris flush took place on the afternoon of June 14.

ESBSs/VBSs:  The last VBS/ESBS video inspections were attempted on May 21.  They were cancelled due to near zero water visibility.  The next inspections are scheduled for later in June.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  Due to high debris levels (lots of sticks) there were numerous debris clogs in the juvenile collection gallery orifices during the week.  Orifice backflushing was increased from every three hours to as frequently as once per hour to help prevent juvenile fish injuries.  It was not necessary to dewater the separator inclined screen to clean debris this week but it was necessary to manually clean it on a frequent basis to keep it clean.

Transportation Facility:  The fish facility remained operational during the report period despite fairly high debris levels.  Raceways were swept prior to fish loading to help remove debris and prevent clogging of the barge loading line.  The smaller mesh raceway tailscreens remained in place during the week due to concerns with impingement of subyearling chinook in the larger mesh (lamprey friendly) tailscreens.  Very few lamprey were found in the raceways during the week and juvenile lamprey passage numbers have likely already peaked for the season.

Transport Summary:   Direct loading operations did not take during the report week due to high river flows making overnight loading operations hazardous.  Every other day fish barging proceeded according to schedule on the even days of the report week.  High river flows and swift currents at the barge loading dock made raceway to barge loading somewhat tricky and fish were loaded as quickly as possible to minimize time at the dock.

Removable Spillway Weir:  The RSW operated as part of the spill plan.  A debris flush was conducted during the afternoon of June 14 to move a large volume of woody material that was accumulating in the forebay.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Granite Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 197.0 | 178.8 | 86.4 | 70.2 | 56.1 | 54.0 | 2.0 | 1.3 |

*Scrollcase temperature

Other

Inline Cooling Water Strainers:  Cooling water strainers were last inspected for lamprey entrainment on May 23.  A total of 183 lamprey were found in the strainers over a combined run time of 3137.5 unit hours.

Invasive Species:  The zebra mussel traps near the adult fishway exit were examined for zebra mussels on June 3.  No evidence of zebra mussels was found.

Research:  Adult fish trap operations continued with a sample rate of 10%.  Scale samples are being taken from one out of every 20 hatchery steelhead.  All wild steelhead and chinook captured are being PIT-tagged and scale and genetic samples taken.  Any previously PIT-tagged steelhead or chinook (either hatchery or wild) will have both scale and genetic samples taken for verification purposes.  Scale samples are also being taken from one out of every three hatchery chinook.  Sort by code Lemhi origin chinook are being radio-tagged and scale and genetic samples taken.

NOAA-Fisheries continued tagging juvenile fish for the transport study and survival study during the week (the extra mortality study has concluded).   The goal of the survival and transport studies is to compare smolt to adult returns of in-river migrating smolts to the smolt to adult returns of transported smolts.  (These two marking studies will conclude early in the next report period.)

Idaho Department of Fish and Game (IDFG) personnel continued genetic stock identification work on chinook and steelhead smolts from the lab during the week.  The goal of the study is to enumerate and characterize the natural production of yearling spring/summer chinook salmon and steelhead above Lower Granite with regard to age composition and genetic stock identification.  IDFG will sample every day until the first part of July with a goal of collecting between 2000 and 4000 genetic samples each from yearling spring/summer chinook and steelhead and 500-1500 genetic samples from subyearling fall Chinook.

The Nez Perce Tribal Fisheries in coordination with the Corps and The University of Idaho continued kelt research work at the holding tanks upstream of the main fish facility.   Clipped and unclipped steelhead kelts are being examined to determine the changes that occur during sexual maturity and to determine post spawning changes associated with successful downstream migration and recovery to spawn again.  Dependent on the group, steelhead kelts are being blood  sampled, PIT-tagged, acoustic-tagged, trucked, barged, or returned back to the river.  (This study is scheduled to conclude in late June.)