U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

#### FISH FACILITIES WEEKLY REPORT

#19 - 2011

# Project:  McNary

# Biologists: Carl Dugger and Bobby Johnson

Dates: July 1 - 7, 2011

## Turbine Operation

McNary had 12 units available for power generation this week.  Units 1 and 10 remain out of service for the rewind contract which will be completed in approximately six months to one year.  On July 5, units 4 and 5 were out of service a total of 50 minutes for ESBS camera inspections.  A failed ESBS was found in 5C slot which was replaced with the unit being out of service for an additional six hours.

The hard constraint one percent criterion continues with no units running outside the criteria.  However, from July 3 to 5, unit 3 ran at the lower end of the criteria due to a VBS differential measurement of 1.5 feet at 3A slot.

## Adult Fish Passage Facilities

On July 2, 4, and 7, the McNary fisheries biologist performed measured inspections of the adult fishways.  Adult fish counting and water temperature monitoring continue.  Also, nightly lowering of Oregon entrance weirs, NFEW2, NFEW3, SFEW1 and SFEW2, for adult lamprey passage continues.  On primary bypass nights, fisheries technicians continue to monitor the entrances to verify weir lowering.  On July 1, video monitoring and adult lamprey counts began.  Finally, the Washington count station received a new air conditioning unit this week.

Fish Ladders:  During measured inspections, all Fish Passage Plan criteria were met on both ladders.

At the Washington ladder’s exit, the picketed leads were constantly monitored by all personnel as debris is still in there area and the leads were cleaned during the day and/or at night as needed.  The fisheries staff cleaned the leads twice during the holiday weekend.  On July 4, the leads were cleaned just before the inspection occurred.  Early in the week, the regulating weir alarmed once and was reset.

At the Oregon exit, the south traveling screen continued to trigger false differential alarms but the occurrence of these alarms has decreased.  For the week, the frequency of screens operation ranged from six to eight times a day.  Measured differential readings revealed no problems.  On July 5, all Oregon exit weirs received scheduled maintenance.

Fishway Entrances and Collection Channel:  On July 4 and 7, Washington ladder entrance weir, W2, measured 7.7 and 6.9 feet, respectively.  Due to spill turbulence, W2 and W3 have been difficult to keep calibrated.  All other inspection points on both ladders were in criteria.  The Oregon ladder’s south powerhouse entrance weir, SFEW2, has a failed LED which has not yet been replaced.  Until then, the dial indicator on the weir cable drum will be used for measurements.  The collection channel velocity, which is affected by high tailwater elevations, averaged 1.5 feet per second.

Auxiliary Water Supply System:  For the week, fish pumps 1 and 3 were in service with blade angles of approximately 30 degrees with no interruptions in service recorded.  Pump 2 remains out of service due to a major overhaul.  The project now estimates the return to service date to be in January, 2012.

The juvenile facility continues to supplying the usual 450 cfs to the north powerhouse pool with no interruptions in service.  Finally, the Wasco County PUD unit was out of service from approximately 0000 to 0500 hours every night of the week due to BPA not requiring the power production.  During all outages, the bypass system operated well.

#### Juvenile Fish Passage Facility

Alternating days of primary and secondary bypass continued for the spring season with the switch occurring every morning at 0700 hours with no disruptions in this schedule.

For the report week, 170,040 smolts and 1,900 juvenile lampreys were bypassed during secondary operations.

Forebay Debris/Gatewell Debris/Oil:  For the week, forebay debris remained light to moderate as debris arrived and dissipated.  However, debris continues to be monitored through out the project.  Trash rack differential monitoring revealed no significant problems and no racks were cleaned.  Repairs to the damaged trash rack hoist and cleaning device continue.

A slight amount of oil was removed from four slots at units 1 and 10 with absorbent pads after the units were removed from service.  The slot at 1B remains dewatered as the issue with the headgate for that slot has not yet been resolved.

ESBSs/VBSs:  ESBSs are deployedat all units except at 1B slot which is dewatered.  Rehabilitation continues on the two spare ESBS’s.  The screens at 2A, 2B, 3B and 9C slots remain in bypass mode.  On July 5, ESBS camera inspections occurred at units 4 and 5.  The biologist found that the screen in 5C slot had failed as the brush mechanism appeared to have not moved in some time.  The screen was replaced that day and was found to have had a failed coupler.  Since the screen motor had been running with lower amp readings since June 21, it’s possible the coupler had failed that day.  The screen had a thin layer of milfoil and a small amount of woody debris on it when it was removed.  Only one juvenile lamprey had been lost in the ESBS bar screen and no other harm to fish was noted.

VBS monitoring revealed three screens out of criteria.  On July 1 and 5, these screens and 15 others were cleaned.  As mentioned above, unit 3 operated at reduced load for two days before the screen in 3A slot was cleaned.  The project has 10 to 12 VBS’s scheduled for rehabilitation and replacement this year.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  Forty two orifices were utilized this week with no blockages observed.  Since the 1B slot is dewatered, a makeup orifice was opened at 2C slot.

All systems operated well in automatic mode.  On July 1, the rectangular screen cleaning device was found jammed on its downstream path.  The biologist was able to reset the mechanism before it alarmed.  The separator technician reported a three-foot long by two-inch diameter stick had arrived at the separator just after the jam was cleared.  Besides during primary bypass and daily checks, the channel was also monitored during VBS cleaning.

Transportation Facility:  Alternating days of primary and secondary bypass continue.  With the spring bypass season, both bypass modes return all fish are to the river.  PIT tag detection occurs in the full flow pipe during primary bypass and throughout the facility during secondary bypass.  Smolt monitoring occurs only on secondary bypass days.  The primary A PIT tag slide gate remains on for the CRITFC study.  The B PIT tag gate remains off and closed as the return to river line provides a better bypass route for PIT tagged fish.  The PIT tag equipment continues to receive weekly checks.  The secondary (C and D) PIT/bypass gates were off and open as there are no studies requiring them this year.  The sample gates were activated and functioned well.  They will be turned off or on at 0700 hours each day so they will function only during secondary bypass.

Ice block checks of the return to river lines removed no blockages.  However, due to high tailwater elevations it is very difficult to see anything exit the secondary bypass line.

Work on a tailscreen hoist for the east raceway bank and fabrication of the new “lamprey friendly” raceway tailscreens continues.

Transport Summary:  There is nothing to report.  However, preparations for transport season have begun.

River Conditions

River conditions during the week are outlined in Table 1 as provided by the smolt monitoring staff whose data day runs from 0700 to 0700 hours.  Clarity data was provided by the control room.  The summer spill program, which targets 50 percent of total flow to be spilled, continued.  Actual spill ranged from 62 to 66 percent of total flow due to high discharge in excess of powerhouse capacity.

Work continues on spill gate 1, which remains out of service with the bay closed.

The smolt monitoring staff continues to gather water temperature data, which will be reported separately.

Table 1.  River conditions at McNary Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 434.2 | 380.2 | 284.6 | 235.3 | 60.5 | 58.5 | 3.0 | 2.2 |

Other

Inline Cooling Water Strainers:  The next cooling water strainer examination will occur in late July.

Invasive Species:  The zebra mussel station examination on July 4 revealed no problems.

Predatory Bird Observations:  Bird counts continue with the forebay area being checked once a day and the tailwater area being checked twice a day.  In the tailwater area, high counts were 76 gulls, 31 pelicans, 10 cormorants and 17 terns.  Most birds were seen in the spill basin with the pelicans along the navigation lock wall apparently feeding on adult shad.  Bypass outfall high counts were six gulls, two terns and two pelicans.  Pelicans were also observed by the adult return outfall.  The water cannon operated well.  Birds are most active during swing shift when hazing personnel were off duty.

In the forebay area, an occasional grebe, tern, cormorant, pelican or osprey was observed.  Occasionally, a large group of gulls was noted by the spill or a large group of grebes was noted south of the powerhouse.  No grebes were seen in the gatewell slots or in the juvenile collection channel.  A large group of pelicans continue to roost on the rocks by the Washington boat dock.

Research:  The study of the Oregon ladder exit area by the traveling screens continued with the fisheries staff assisting in monitoring the debris trap at night when primary bypass is occurring.  The debris trap is not currently in use during secondary bypass nights due to the in-river debris loads.  Preparations for the adult lamprey passage study are also on going with cameras already installed at the ladders’ picketed leads.  Gas bubble trauma examinations continue and results can be requested from the smolt monitoring staff.  The ODFW angling survey for small mouth bass in the project’s tailwater and forebay adjacent to the powerhouse also continued.  Finally, CRITFC study designed to monitor PIT tagged fish with cameras continues but the biologist has had a programming issue with their system.

Fish Salvage Operations: On July 1, the unit 1 scroll case was dewatered.  Salvaged fish included three adult channel catfish salvaged and one subyearling Chinook smolt.  All were returned to the river.  On July 6,the unit 1 draft tube was dewatered and 16 to 20 adult channel catfish were recovered.  Approximately six of the catfish recovered were old mortalities.

Project:  Ice Harbor

Biologist: Mark Plummer

Biological Technician: Stephen Jeffers

Dates: July 1 - 7, 2011

## Turbine Operation

All turbine units were available for operation this reporting period.  Turbine unit 3 went out of service for annual maintenance July 5 at 0633 hours.

## Adult Fish Passage Facilities

### Fish facility personnel inspected the adult and juvenile fish passage ways July 5, 6, and 7.

### Fish Ladders:  All north and south adult fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria. The adult collection channel velocity meter is not functioning.   Installation of the new equipment cannot be completed until the adult south fish ladder is unwatered this winter maintenance period.

### Fishway Entrances and Collection Channel (inspection date order):  The south shore entrance (SFE) was off sill with a depth of 8.7 feet, off sill with a depth of 8.9 feet, and off sill with a depth of 8.6 feet.  The north powerhouse entrance (NFE) was off sill with a depth of 9.6 feet, off sill with a depth of 10.1 feet, and off sill with a depth of 8.5 feet.  The north shore entrance (NSE) was on sill with a depth of 14.7 feet, on sill with a depth of 15.1 feet, and on sill with a depth of 14.2 feet.  Fishway entrance criterion is 8 feet depth, greater than 8 feet depth, or on sill.  All channel/tailwater differentials were in criteria, except on July 6 and 7.  On these inspections, the visual north adult fish ladder channel/tailwater elevations were 0.6 feet and 0.5 feet respectively.  The adult fish way computer system indicated the elevations at 1.2 feet on both inspection days. Spill makes reading the staff gage difficult due to fluctuating water elevations at the gage.  The north adult fish entrance weir lifting mechanism has failed.  The adult entrance weir has fallen to sill at 332.2 fmsl.  High river flows are maintaining adult passage criteria at this entrance.  Plans are to repair the entrance hoisting mechanism when the water flows reduce.  Channel/tailwater differential criteria are 1 – 2 feet.  Repairs will be made when river flows lower and access to the entrance weir can be accomplished.

### Auxiliary Water Supply System:  Normally, 2 of the 3 north shore fish pumps are operated.  All north shore fish pumps were available for operation.  North shore fish pumps 1 and 3 were turned off July 7 from 1220 hours to 1340 hours to aid in a video inspection of the failed north shore fish ladder entrance weir.  South shore fish pump 1 remains out of service due to vibration issues at the gearbox shaft.  Currently, 6 of 8 south shore fish pumps are operating satisfactorily.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  No problems to report.  Debris is accumulating in the forebay.  Fish ladder exits are clear of debris and the bubblers are operating.  Approximately 2 cubic yards of debris were removed from turbine unit 1 A slot and C slot June 29.

STSs/VBSs:  The STS rotations are in continuous run mode as the average length of both the subyearling Chinook and the migratory sockeye is below 120 mm.  No problems were observed during the June STS inspections.  Water clarity was very low.  July STS inspections are scheduled for July 11 and 13.

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe:   The juvenile fish bypass is in operation.  20 orifices are open.

Juvenile Bypass Facility:  The bypass was put into operation March 23.

Fish Sampling:  Juvenile fish sample days are Monday and Thursday through the beginning of July.  Fish sampling for the 2011 season concluded July 7.

Removable Spillway Weir:  The RSW is in operation.

Fish Sampling:

July 5:

| Species | Sampled | #Descaled | Morts | Avian Marks |
| --- | --- | --- | --- | --- |
| C-CH | --- | --- | --- | --- |
| UC-CH | --- | --- | --- | --- |
| C-CH-O | 26 | 0 | 0 | 0 |
| UC-CH-O | 98 | 3 | 0 | 1 |
| C-SH | 1 | 0 | 0 | 0 |
| UC-SH | 1 | 0 | 0 | 0 |
| C-COHO | --- | --- | --- | --- |
| UC-COHO | --- | --- | --- | --- |
| C-SOCK | --- | --- | --- | --- |
| UC-SOCK | --- | --- | --- | --- |
| TOTAL | 126 | 3 | 0 | 1 |

July 7:

| Species | Sampled | #Descaled | Morts | Avian Marks |
| --- | --- | --- | --- | --- |
| C-CH | --- | --- | --- | --- |
| UC-CH | --- | --- | --- | --- |
| C-CH-O | 8 | 0 | 0 | 0 |
| UC-CH-O | 55 | 0 | 1 | 0 |
| C-SH | 3 | 0 | 0 | 0 |
| UC-SH | 1 | 0 | 0 | 0 |
| C-COHO | --- | --- | --- | --- |
| UC-COHO | --- | --- | --- | --- |
| C-SOCK | --- | --- | --- | --- |
| UC-SOCK | --- | --- | --- | --- |
| TOTAL | 67 | 0 | 1 | 0 |

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Ice Harbor Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 179.6 | 131.6 | 96.6 | 63.0 | 59 | 57 | 2.6 | 2.0 |

*Unit 1 scrollcase temperature.

Other

Inline Cooling Water Strainers:  Cooling water strainers were last inspected June 21.  No fish were seen or recovered.

Invasive Species:  No zebra mussels were observed during this report period.

Spill for fish begin April 3, 2011.

# Project:  Lower Monumental Dam

# Biologists:  William Spurgeon and Elizabeth Lindsey

Dates: July 1 - 7, 2011

## Turbine Operation

The units are being operated in hard constraint of the 1% operation criteria.  Unit 6 was taken out of service on June 28 at 0701 hours for annual maintenance.  Units 1, 2, and 3 were rotated out of service for STS and VBS inspections on July 5 and 6.  Unit 3 was taken out of service due to a damaged STS in gatewell slot 3C at 1455 hours on July 6.  The unit was returned to service at 1435 hours on July 7.

Adult Fish Passage Facility

The adult fishway was inspected by Corps and PSMFC biologists on July 1, 2, and 6.

Fish Ladders:  Fishway exit head differentials and depths over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively) on all inspections.  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively) during all inspections.

### Fishway Entrances and Collection Channel:  NSE 1 and NSE 2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections.  North shore channel/tailwater head was in criteria (1’-2’) during all inspections.

SPE 1 and SPE 2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections.  South powerhouse channel/tailwater head was in criteria (1’-2’) during all inspections.

SSE1 weir gate was in depth criteria (criteria: > 8’ or on sill) on all inspections.  SSE 2 was in criteria (6’ above sill) on all inspections.  South shore channel/tailwater head was in criteria (1’-2’) this week.

### Auxiliary Water Supply System:  All AWS pumps were in service and operating throughout this period.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 433.3 square yards of forebay debris observed during this period.  Gatewell debris ranged from 0-30% surface coverage.  No oil was observed in gatewells.

STSs/VBSs:  STS operations remained in continuous run mode as average fork length of sub-yearling Chinook and/or sockeye is less than 120mm.  STSs and VBSs in units 6, 1, 2, and 3 were inspected on July 5 and 6.  Inspection of unit 3 STSs revealed the screen in gatewell slot C required repair. The screen was replaced July 7th.  All other screens were in good operating condition.

Orifices, Collection Channel, Dewatering Structure, Flume:  The collection channel is operating with 20 orifices open.  The mechanical cleaner in the primary dewatering structure remains out of service.  The cause of this outage is undetermined and a trouble report has been submitted.  The pneumatic screen cleaner has been set to cycle every 10 minutes and is typically more than adequate for removing debris from the screen.  Due to high levels of leafy debris this week, the mechanical screen cleaner is being operated manually on an hourly basis in addition to the bubbler system.

Collection Facility:  The collection facility was switched to primary bypass on July 6 from 1538 to 1600 hours for the removal of built up debris from the primary dewaterer screens.  Debris had accumulated from the mechanical screen cleaner and concern was that the debris buildup would plug the fish separator if not byassed.  No other problems occurred this week.

Transport Summary:  Alternate day transport is occurring with barges arriving on even numbered days.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Monumental Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF)* |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 171.7 | 126.0 | 74.2 | 40.8 | 61.0 | 59.0 | 2.5 | 1.2 |

*Scrollcase temperatures.

#### Other

Inline Cooling Water Strainers:  Cooling water strainers were inspected on July 5.  No live lamprey was recovered.  Mortalities included 23 lamprey, 0 salmon smolts, 0 juvenile steelhead, 0 Siberian prawns, and 11 shad.

Invasive Species:  There were no zebra mussels observed at the monitoring stations on July 1.

Pelican presence at the bypass outfall pipe has been infrequent.

Project:  Little Goose

# Biologist: George Melanson

Dates: July 1 - 7, 2011

## Turbine Operation

Turbine units 1 through 4 and 6 were available for service throughout the report period.   Turbine unit 5 was removed from service for annual maintenance on July 5.  For the most part, all turbine operations were within 1% of best efficiency.  Turbine unit 1 operated outside the criteria on July 6 from 0211 to 0228 hours.

## Adult Fish Passage Facility

COE and ODFW fisheries biologists performed measured inspections of the adult fishway July 1, 5, and 7.

Fish Ladder:  The ladder exit head differentials ranged between 0 and 0.2 feet on all three inspections (criteria < 0.5 ft.).  Water depths over the weirs ranged between 1.0 and 1.1 feet (criteria 1.0-1.3 ft.) and picketed lead head differentials ranged between 0 and 0.1feet (criteria < 0.3 ft.).  No debris was observed at the picketed leads or the ladder exit.  The air bubbler used to prevent debris from collecting near the ladder exit operated satisfactorily.

Fishway Entrances and Collection Channel:  Channel to tailwater head differentials ranged between 1.24 and 2.10 feet (criteria 1.0 to 2.0 ft.).  SSE weir depths ranged between 8.16 and 8.60 feet (criteria ≥8.0 ft), NPE weirs ranged between 6.98 (sill) and 7.14 feet (criteria ≥7.0 ft or on sill).  NSE weirs remain at fixed elevations of 531.5 feet and depths ranged between 6.92 and 8.0 feet (criteria ≥ 6.0 ft.).  Collection channel surface water velocities (criteria 1.5 fps) ranged from 1.8 to 2.1 fps near the SSE.  NSE was not recorded this week due to closure of North shore area.

Auxiliary Water Supply System:  All fish pumps operated in criteria.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:   Up to 14,400 square feet of woody debris has collected in front of the turbine intakes.  Small debris continued to be problematic in a few gatewell orifices and hand removal of debris continued from gatewells.

Spillway Weir:  The spillway weir continued to operate in the low crest position.

ESBS/VBS:   All ESBS operated within criteria this report period.  Drawdown measurements on turbine units 1 through 4 and 6 were performed on July 7.  All measurements were in criteria.  Video inspections were performed to turbine unit 5 ESBS and VBS.  All screens were observed to be in good operating condition.

Orifices, Collection Channel, Dewatering Structure, Flume:  The juvenile collection system operated within criteria with 21 open orifices.  Several orifices blockages occurred this report period and increased orifices inspections and back-flushing continued.

Transportation Facility:  Daily collection for this period ranged between 3,321 and 15,767 for a total of 60,514 for the week.  All fish were transported except for mortalities and several fry that were bypassed.  Descaling and mortality rates for this report period are 0.3% and 0.3% respectively.

Transport Summary:  Every other day barging operations were successfully performed this report period.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Little Goose Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 161.1 | 123.9 | 52.1 | 37.5 | 60.3 | 57.2 | 2.9 | 2.2 |

*Ladder temperature.

Other

Invasive Species:  The zebra mussel substrate monitor was inspected on June 2.  No mussels were observed.  The next inspection is scheduled for July 15.

Cooling Water Strainers:  Cooling water strainers on all units were inspected on July 7, 13 juvenile Lamprey were found.

Avian Activity: The occasional gull and cormorant were observed in the vicinity of the dam.

Project:  Lower Granite

# Biologists:  Mike Halter and Ches Brooks

Dates: July 1 - 7, 2011

## Turbine Operation

Lower Granite had turbine units 1-3 and 5-6 available for power generation at the beginning of the report week.  On June 30, turbine unit 4 was taken out of service at 2342 hours due to a field ground fault, the unit was returned to service at 1004 hours on July 1.  On July 5 at 0603 hours turbine unit 6 was taken out of service, as scheduled, in order to conduct exciter rehabilitation and annual maintenance.  The tentative return to service date for this unit is August 19.  All available units were run within the operational guidelines.

## Adult Fish Passage Facility

On July 2, 3, and 4 the Lower Granite COE fisheries biologists performed measured inspections of the adult fishway system.

Fish Ladder:  All criteria were met with the exception of the diffuser 14 reading which remained between 727.9 and 727.8 feet on all inspections (0.1 – 0.2 feet below criteria).

Fishway Entrances and Collection Channel:  Problems developed with the weir motor and cable control system on north shore fishway entrance number 1 (NSE-1) on the morning of May 31.  Inspection revealed that the cable had broken and the weir gate had dropped to the sill.  The weir motor was also burned up.  A temporary adjustment was done on the weir gate by crane on June 7 and the gate was dogged off at 635.0 feet by cables.  This setting will be maintained until an A-frame and chain hoist system can be put in place to adjust the weir depth relative to the tailwater elevation.  Head differential readings remained within criteria during all fishway inspections this week. Weir depths at the south shore fishway entrances remained within criteria on all inspections. Weir depth readings at the north powerhouse fishway entrances also remained within criteria on all inspections.  Weir depths at the north shore fishway entrances were out of criteria on all inspections this week.  The readings on NSE-1 were off the scale (due to the temporary cable fix) while the readings on NSE-2 ranged from 4.7 to 5.1 feet (criteria ≥ 7.0 feet).  Velocity readings in the adult fishway collection channel transition pool area ranged from 0.83 to 1.06 feet per second and averaged 0.92 feet per second.

### Auxiliary Water Supply System:  There were no problems with the auxiliary water system during the report week.   Fish pumps one and two were run all week.

#### Juvenile Fish Passage Facility

The juvenile fish facility sample rate was increased from 4.0% to 10.0% at 0700 hours on July 4.

Forebay Debris/Gatewell Debris/Oil:  The amount of forebay debris varied during the week due to wind strength and direction; none was removed.

ESBSs/VBSs:  The last VBS/ESBS video inspections were attempted on June 24-25.  They were cancelled due to near zero water visibility and concerns with the increased spill levels (due to the need to shut off units one at a time) increasing dissolved gas levels.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  Juvenile fish collection gallery orifices were backflushed at regular 3 hour intervals all week.  Vegetative debris levels increased considerably from the previous report week and caused some issues at the fish facility.  The increase in vegetative debris made it necessary to partially open the separator bypass valve on seven occasions for approximately 15 to 20 minutes during shifts on the dates July 5-8 to help move debris off the separator inclined screen. On occasions of partial clogs the separator technicians were able to clear the screen with the power air rake tool that the maintenance staff developed.

Transportation Facility:  The fish transportation facility operated well during the week despite debris issues.  Raceways were swept prior to barge loading and a considerable amount of vegetative material removed.  The facility switched from the standard smaller mesh raceway tailscreens back to the larger mesh tailscreens after lamprey were noticed in the raceways.

Transport Summary:   Direct loading operations did not take during the report week due to high river flows making overnight loading operations hazardous.  Every other day fish barging proceeded according to schedule on the even days of the report week.  Operations went smoothly all week.

Removable Spillway Weir:  The RSW operated normally as part of the spill plan.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Granite Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 168.1 | 131.7 | 75.8 | 34.4 | 60.3 | 58.7 | 2.3 | 2.1 |

*Scrollcase temperature.

Other

Inline Cooling Water Strainers:  Cooling water strainers were last inspected for lamprey entrainment on June 27.  A total of 38 lamprey were found in the strainers over a combined run time of 3998.6 unit hours.  Unit 6 strainers were not inspected due to a B.P.A. request.

Invasive Species:  The zebra mussel traps near the adult fishway exit were last examined for zebra mussels on the June 30 inspection.  No evidence of zebra mussels was found.

Turbine Unit Dewatering:  A fish salvage operation took place in the scroll case of turbine unit #6 between 1245 and 1315 hours on July 6.  Only one rainbow trout (hatchery) of approximately 10 inches in length was found in the scroll case.  It was released alive into the dam tailrace area.

Research:  Adult fish trap operations continued with a sample rate of 10%.  Scale samples are being taken from one out of every 20 hatchery steelhead.  All wild steelhead and Chinook captured are being PIT-tagged and scale and genetic samples taken.  Any previously PIT-tagged steelhead or Chinook (either hatchery or wild) will have both scale and genetic samples taken for verification purposes.  Scale samples are also being taken from one out of every three hatchery Chinook.  Sort by code Lemhi origin Chinook are being radio-tagged and scale and genetic samples taken.

NOAA-Fisheries concluded tagging juvenile fish for the transport study and survival study on June 17.   The goal of the two studies is to compare smolt to adult returns of in-river migrating smolts to the smolt to adult returns of transported smolts.  NOAA will begin tagging fall Chinook in the JFF lab to evaluate late season transport in late August or early September.

Idaho Department of Fish and Game (IDFG) personnel continued genetic stock identification work on Chinook and steelhead smolts from the lab during the week.  The goal of the study is to enumerate and characterize the natural production of yearling spring/summer Chinook salmon and steelhead above Lower Granite with regard to age composition and genetic stock identification.  IDFG will sample every day until the first part of July with a goal of collecting between 2000 and 4000 genetic samples each from yearling spring/summer Chinook and steelhead and 500-1500 genetic samples from subyearling fall Chinook.

The Nez Perce Tribal Fisheries in coordination with the Corps and The University of Idaho concluded kelt research work at the holding tanks upstream of the main fish facility on June 30.   Clipped and unclipped steelhead kelts were examined to determine the changes that occur during sexual maturity and to determine post spawning changes associated with successful downstream migration and recovery to spawn again.  Dependent on the group, steelhead kelts were blood sampled, PIT-tagged, acoustic-tagged, trucked, barged, or returned back to the river.