U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

#### FISH FACILITIES WEEKLY REPORT

#20 - 2011

# Project:  McNary

# Biologists: Carl Dugger and Bobby Johnson

Dates: July 8 - 14, 2011

## Turbine Operation

McNary had nine to 12 units available for power generation this week.  Units 1 and 10 remain out of service for the rewind contract which will be completed in approximately six months to one year.  On July 8, unit 13 was out of service 9.3 hours due to a failed ESBS in 13A slot requiring repair.  Later that day, the ESBS failed again resulting in the unit being out of service until the next day when the fish screen was replaced.  On July 11, unit 7 was removed from service until approximately July 31 for field testing.  On July 12, unit 6 was out of service for one hour for ESBS camera inspections and resetting an electrical trip.  On July 13, as part of the unit 7 testing, unit 8 was removed from service.  From July 13 to 14, unit 6 was out of service for hub tapping and removal of hydraulic fluid from 6B slot.  While raising the headgate at 6B slot, hydraulic fluid was noted in the gatewell slot.  Later, it was determined that the main hydraulic leak was at station service unit 01.  Both sites were isolated and the fluid was removed, with none entering the river.  Unit 6 was able to return to service and the headgate at the station service unit will be repaired.

The hard constraint one percent criterion continues with no units running outside the criteria.

## Adult Fish Passage Facilities

On July 9, 11, and 14, the McNary fisheries biologist performed measured inspections of the adult fishways.  Adult fish counting including video review for lamprey, water temperature monitoring, and nightly lowering of Oregon entrance weirs, NFEW2, NFEW3, SFEW1 and SFEW2, for lamprey passage continue.  On primary bypass nights, fisheries technicians will monitor the entrances to verify that the weirs are lowering.

Fish Ladders:  During measured inspections, all Fish Passage Plan criteria were met on both ladders.

At the Washington ladder’s exit, the picketed leads were constantly monitored by all personnel and the leads were cleaned during the day and/or at night as needed.  On July 10, the fisheries staff cleaned the leads.  However, debris in the area has decreased.  On July 13, all exit weirs received scheduled maintenance.

At the Oregon exit, the south traveling screen had one false differential alarm.  The frequency of screen operation was set at eight times a day.  The screen’s wash pump also triggered an alarm which was reset.  Measured differential readings revealed no problems.

Fishway Entrances and Collection Channel:  All week, Washington ladder entrance weir, W2, measured 6.9 to 7.9 feet possibly due to calibration drifts caused by spill turbulence.  On July 14, W2 and W3 were calibrated.  All other inspection points on both ladders were in criteria.  The Oregon ladder south powerhouse entrance weir, SFEW2, has a failed LED which has not yet been replaced.  Until then, the dial indicator on the weir cable drum will be used for measurements.  The collection channel velocity averaged 1.7 feet per second.

Auxiliary Water Supply System:  For the week, fish pumps 1 and 3 were operated with blade angles of approximately 30 degrees with no interruptions in service recorded.  Pump 2 remains out of service due to a major overhaul.  The project now estimates the return to service date to be January 31, 2012.

The juvenile facility continues to supplying the usual 450 cfs to the north powerhouse pool with no interruptions in service.  Finally, the Wasco County PUD unit was out of service from approximately 0000 to 0500 hours every night of the week due to BPA not requiring the power production.  During all outages, the bypass system operated well.

#### Juvenile Fish Passage Facility

Alternating days of primary and secondary bypass continue for the spring season with the switch occurring every morning at 0700 hours.  There were no interruptions from this schedule.

For the report week, 220,846 smolts and 1,877 juvenile lampreys were bypassed during secondary operations.

Forebay Debris/Gatewell Debris/Oil:  For the week, forebay debris remained light as most debris dissipated after arrival.  However, debris continues to be monitored throughout the project with most debris being on the upstream face of the spillway.  Trash rack differential monitoring revealed no significant problems and no racks were cleaned.  Repairs to the damaged trash rack hoist and cleaning rake continue.

As mentioned above, hydraulic fluid was removed from 6B slot and station service unit 01 on July 13 and 14.  No other problems were seen.  The slot at 1B remains dewatered as the issue with the headgate for that slot has not yet been resolved.

ESBSs/VBSs:  ESBSs are deployed in all units except at 1B and 10B slots.  Rehabilitation continues on the two spare ESBSs.  The screens in 2A, 2B, 3B and 9C slots remain in bypass mode.  On July 8, the screen at 13A slot failed.  The electrical cable was repaired and the screen was returned to service only to fail again later that day.  On July 9, the ESBS in 13A slot was replaced with the ESBS from 10B slot.  Following installation and the triggering of alarms, the new screen in 13A slot was switched to bypass mode were it remains.  ESBS camera inspections at units 6 and 7 revealed no problems.

VBS differential monitoring revealed five screens out of criteria.  On July 8, 9 and 11, these screens and nine others were cleaned.  The project has 10 to 12 VBS’s scheduled for rehabilitation and replacement this year.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  Forty two orifices were utilized this week with no blockages observed.  Since 1B slot is dewatered, a make-up orifice was previously opened at 1C slot.  During the removal of hydraulic fluid from 6B slot, all unit 6 orifices were closed and makeup orifices were opened at unit 7.  Station service 01 has no orifices.  However, the juvenile facility emergency water supply lines feed from this unit.  During the removal of the fluid, these supply lines were also closed.

All system operated well in automatic mode.  On July 11, installation of an alarm for the channel PLC’s new uninterrupted power supply occurred.  Besides during primary bypass and daily checks, the channel was also monitored during VBS cleaning and hydraulic oil removal.

Transportation Facility:  Alternating days of primary and secondary bypass continue.  With the spring bypass season, both bypass modes return all fish are to the river.  PIT tag detection  occurs in the full flow pipe during primary bypass and throughout the facility during secondary bypass.  Smolt monitoring occurs only on secondary bypass days.  The primary A PIT tag slide gate remains on for the CRITFC study.  The B PIT tag gate remains off and closed as the return to river line provides a better bypass route for PIT tagged fish.  The PIT tag equipment continues to receive weekly checks.  The secondary (C and D) PIT/bypass gates were off and open as there are no studies requiring them this year.  The sample gates functioned well.  They are turned off or on at 0700 hours each day so they will function only during secondary bypass operations.

On July 11, at 1300 hours, the sample rate was reduced from two to 0.5 percent to avoid excess fish in the sample collection.

Ice block checks of the return to river lines removed one small blockage from the A line this week.

Work on a tailscreen hoist for the east raceway bank and fabrication of new raceway tailscreens that will pass juvenile lamprey continues.

Transport Summary:  Preparations for transport season have begun.

River Conditions

River conditions during the week are outlined in Table 1 as provide by the smolt monitoring staff whose data day runs from 0700 to 0700 hours.  Clarity data was provided by the control room.  The summer spill program, which targets 50 percent of total flow to be spilled, continues.  Actual spill ranged from 57 to 65 percent of total flow due to high discharge in excess of powerhouse capacity.

Spill gate 1, which remains out of service, is scheduled to return to service on July 21.

The smolt monitoring staff continues to gather water temperature data which is reported in a separate document.

Table 1.  River conditions at McNary Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 401.1 | 318.6 | 254.8 | 181.9 | 61.5 | 60.3 | 4.6 | 3.5 |

Other

Inline Cooling Water Strainers:  The next cooling water strainer examination will occur in late July.

Invasive Species:  The next zebra mussel station examination will occur in early August.

Predatory Bird Observations:  Bird counts continue with the forebay area being checked once a day and the tailwater area being checked twice a day.  In the tailwater area, high counts were 85 gulls, 58 pelicans, 30 cormorants and 20 terns.  Most birds were seen in the spill basin with the pelicans along the navigation lock wall apparently feeding on adult shad.  By the bypass outfalls, the high counts were 12 gulls, three terns and three pelicans.  Pelicans were also observed by the adult return outfall.  The water cannon operated well.  Birds were the most active during swing shift when hazing personnel were off duty.  The hazing contract will conclude July 16.

In the forebay area, an occasional grebe, tern, gull, cormorant, pelican or osprey was observed.  No grebes were seen in the gatewell slots or in the juvenile collection channel.  A large group of pelicans continue to roost on the rocks by the Washington boat dock.

Research:  The study of the Oregon ladder exit area by the traveling screens continues with the fisheries staff assisting in monitoring the debris trap at night when primary bypass is occurring.  The debris trap is no currently in use during secondary bypass nights due to the in river debris loads.  Preparations for the adult lamprey passage study are also ongoing with cameras already installed at the count station picketed leads.  Gas bubble trauma (GBT) examinations continue.  Results can be requested from the smolt monitoring staff.  The ODFW angling survey for small mouth bass in the tailrace and forebay areas adjacent to the powerhouse also continues.  Finally, CRITFC study designed to monitor PIT tagged fish with cameras continues and the biologist expects to resolve programming issues on July 15.

Fish Salvage Operations:  The unit 7 scroll case was dewatered July 12 and no fish were found.  This was followed by the unwatering of the associated draft tube on July 13. Twelve adult channel catfish along with one 3.5 foot sturgeon were salvaged.  No mortalities were found.

Project:  Ice Harbor

Biologist: Mark Plummer

Biological Technician: Stephen Jeffers

Dates: July 8 - 14, 2011

## Turbine Operation

All turbine units were available for operation this reporting period.  Turbine unit 3 remains out of service for annual maintenance.  Turbine units 1, 5, and 6 were out of service for short periods while the STS and cooling water strainer inspections were performed July 11.  Turbine unit 4 went out of service July 12 at 0659 hours for scheduled Doble testing and required cleaning of the transformer and buss work insulators on line 2.  Turbine unit 2 STS and cooling water strainer inspections were performed July 13.   Turbine units 3 and 4 were also inspected, however they were already out of service for other reasons.

## Adult Fish Passage Facilities

### Fish facility personnel inspected the adult and juvenile fish passage ways July 12, 13, and 14.

### Fish Ladders:  All north and south adult fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria. The adult collection channel velocity meter is not functioning.  The current method of monitoring the velocity is channel/tailwater differential, floatation device timing, and visual observation.

### Fishway Entrances and Collection Channel (inspection date order):  The south shore entrance (SFE) was off sill with a depth of 9.8 feet, off sill with a depth of 9.5 feet, and off sill with a depth of 9.4 feet.  The north powerhouse entrance (NFE) was off sill with a depth of 8.7 feet, off sill with a depth of 7.5 feet, and off sill with a depth of 7.2 feet.  The north shore entrance (NSE) was on sill with a depth of 12.0 feet, on sill with a depth of 11.2 feet, and on sill with a depth of 13.7 feet.  Fishway entrance criterion is 8 feet depth, greater than 8 feet depth, or on sill.  The entrance weir depth out of criteria at the NFE July 13 and 14 were reported to the shift operator to make adjustments.  All channel/tailwater differentials were in criteria, except July 13.  On this inspection, the visual north adult fish ladder channel/tailwater elevation was 0.9 feet and the computer indication was 0.96.  This cannot be adjusted as the north adult fish entrance weir lifting mechanism has failed.  The adult entrance weir has fallen to sill at 332.2 fmsl.  High river flows are maintaining adult passage criteria at this entrance.  Plans are to repair the entrance hoisting mechanism when the water flows reduce.  Channel/tailwater differential criteria are 1 – 2 feet.  Repairs will be made when river flows lower and access to the entrance weir can be accomplished.

### Auxiliary Water Supply System:  Normally, 2 of the 3 north shore fish pumps are operated.  All north shore fish pumps were available for operation.  South shore fish pump 1 remains out of service due to vibration issues at the gearbox shaft.  Currently, 6 of 8 south shore fish pumps are operating.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  No problems to report.  Debris is accumulating in the forebay.  Fish ladder exits are clear of debris and the bubblers are operating satisfactorily.

STSs/VBSs:  All STSs are in continuous run mode due as the average length of both subyearling Chinook and migratory sockeye is below 120 mm.  No problems were observed during the July STS inspections.  August STS inspections are scheduled for August 9 and 10.

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe:   The juvenile fish bypass is in operation.  20 orifices are open.

Juvenile Bypass Facility:  The bypass was put into operation March 23.

Fish Sampling:  Juvenile fish sample days are Monday and Thursday through the beginning of July.  Fish sampling for the 2011 season concluded July 7.

Removable Spillway Weir:  The RSW is in operation.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Ice Harbor Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 125.6 | 92.8 | 62.3 | 37.8 | 62 | 60 | 3.4 | 2.6 |

*Unit 1 scrollcase temperature.

Other

Inline Cooling Water Strainers:  Cooling water strainers were last inspected June 21.  No juvenile lamprey were found.

Invasive Species:  No zebra mussels were observed during this period.

Spill for fish begin April 3, 2011.

# Project:  Lower Monumental Dam

# Biologists:  William Spurgeon and Elizabeth Lindsey

Dates: July 8 - 14, 2011

## Turbine Operation

All units are being operated in hard constraint of the 1% operation criteria.  Unit 6 was taken out of service on June 28 at 0701 hours for annual maintenance.  Units 4 and 5 were rotated out of service for STS and VBS inspections on July 11 and 12.

Adult Fish Passage Facility

The adult fishway was inspected by Corps and PSMFC biologists on July 8, 9, 10 and 13.

Fish Ladders: Fishway exit head differentials and depths over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively) on all inspections.  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively) on all inspections.

### Fishway Entrances and Collection Channel: NSE 1 and NSE 2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections.  North shore channel/tailwater head was in criteria (1’-2’) on all inspections.

SPE 1 and SPE 2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections.  South powerhouse channel/tailwater head was in criteria (1’-2’) on all inspections.

SSE1 weir gate was in depth criteria (criteria: > 8’ or on sill) on all inspections.  SSE 2 was in criteria (6’ above sill) on all inspections.  South shore channel/tailwater head was in criteria (1’-2’) this week.

### Auxiliary Water Supply System:  All AWS pumps were in service and operating throughout this period.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 575.8 square yards of forebay debris observed during this period.  Gatewell debris ranged from 0-25% surface coverage.  No oil was observed in gatewells.

STSs/VBSs:  STS operation remained in continuous run mode as average fork length of sub-yearling chinook and/or sockeye is less than 120mm.  STSs and VBSs associated with units 4 and 5 were inspected on July 11 and 12.  Inspection revealed no problems.  STS/VBS inspections for the month of July are now complete.

Orifices, Collection Channel, Dewatering Structure, Flume:  The collection channel is operating with 20 orifices open.  The primary dewatering structure mechanical screen cleaner continues to malfunction when set in automatic operation mode.  Facility personnel discovered that the metal connector attaching the electric motor to its brake assembly has broken.  Replacements parts have been ordered. The pneumatic screen cleaner has been set to cycle every 10 minutes and is typically more than adequate for removing debris from the screen.  Due to high levels of leafy debris, the mechanical screen cleaner is being operated manually on an hourly basis in addition to bubbler system operation.

Collection Facility:  The collection facility was switched to primary bypass on July 9 at 1635 hours due to a debris obstruction in the separator adult release pipe.  The facility resumed collection on July 10 at 1130 hours after the pipe was disassembled and the obstruction was removed.  No other problems occurred this week.

Transport Summary:  Alternate day transport is occurring with barges arriving on even numbered days.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Monumental Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF)* |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 120.1 | 89.4 | 23.8 | 16.9 | 62.0 | 61.5 | 3.2 | 3.0 |

*Scrollcase temperatures.

#### Other

Inline Cooling Water Strainers:  Cooling water strainers were inspected on July 5.  No live lamprey was recovered.  Mortalities included 23 lamprey, 0 salmon smolts, 0 juvenile steelhead, 0 Siberian prawns, and 11 shad.

Invasive Species:  There were no zebra mussels observed at the monitoring stations on July 1.

Pelican presence at the bypass outfall has been infrequent.

Project:  Little Goose

# Biologist: George Melanson

Dates: July 8 - 14, 2011

## Turbine Operation

Turbine units 1 through 4 and 6 were available for service throughout the report period.   Turbine unit 5, remained out of service for scheduled annual maintenance.  All turbine operations were within 1% of best efficiency.

## Adult Fish Passage Facility

COE and ODFW fisheries biologists performed measured inspections of the adult fishway July 8, 10 and 12.

Fish Ladder:  The ladder exit head differentials ranged between 0.0 and 0.2 feet (criteria < 0.5 ft.).  Water depths over the weirs ranged between 1.0 and 1.1 feet (criteria 1.0-1.3 ft.) and picketed lead head differentials measured no differential during all three inspections (criteria < 0.3 ft.).  No debris was observed at the picketed leads or the ladder exit.  The air bubbler used to prevent debris from collecting near the ladder exit operated satisfactorily.

Fishway Entrances and Collection Channel:  Channel to tailwater head differentials ranged between 1.34 and 1.98 feet (criteria 1.0 to 2.0 ft.).  SSE weir depths ranged between 8.28 and 8.54 feet (criteria ≥8.0 ft), NPE weirs were on sill and depths ranged between 6.00 and 6.40 feet (criteria ≥7.0 ft or on sill).  NSE weirs remain at fixed elevations of 531.5 feet and depths ranged between 6.14 and 6.56 feet (criteria ≥ 6.0 ft.).  Collection channel surface water velocities (criteria 1.5 fps) ranged from 1.5 to 2.4 fps near the SSE.  NSE was not recorded this week due to the safety closure of North shore area.

Auxiliary Water Supply System:  All fish pumps operated in criteria.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:   Up to 7,000 square feet of woody debris remains in front of the turbine intakes.  Small debris continued to be problematic in a few gatewell orifices and hand removal of debris continued from gatewells.

Spillway Weir:  The spillway weir continued to operate in the low crest position.

ESBS/VBS:   All ESBS operated within criteria this report period.  Drawdown measurements across trashracks and ESBS/VBS were performed on all intakes associated with turbine units 1 through 4.  A measurements were within criteria.

Orifices, Collection Channel, Dewatering Structure, Flume:  The juvenile collection system operated in criteria with 22 open orifices.  Increased orifices inspections and back-flushing continued.

Transportation Facility:  Daily collection for this period ranged between 2,360 and 6,745 for a total of 24,483 for the week.  All fish were transported except for mortalities and several fry that were bypassed.  Descaling and mortality rates for this report period are 0.21% and 0.35% respectively.

Transport Summary:  Every other day barging operations were successfully performed this report period.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Little Goose Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 118.0 | 88.8 | 36.3 | 26.5 | 61.9 | 61.1 | 3.3 | 2.6 |

*Ladder temperature.

Other

Inline Cooling Water Strainers:  Cooling water strainers on all units were inspected on July 13, six juvenile lamprey were found.

Invasive Species:  The Zebra Mussel substrate monitor was inspected on July 12.  No mussels were observed.  The next inspection is scheduled for August 10.

Avian Activity: Up to 10 gulls and 2 cormorants have been observed in the vicinity of the dam.

Project:  Lower Granite

# Biologists:  Mike Halter and Ches Brooks

Dates: July 8 - 14, 2011

## Turbine Operation

Lower Granite had turbine units 1-5 available for power generation at the beginning of the report week.  Turbine unit 6 is undergoing exciter rehabilitation.  The tentative return to service date for this unit is August 19.  All operating units were run within the operational guidelines.

## Adult Fish Passage Facility

On July 9, 10, 11, and 13 the Lower Granite COE fisheries biologists performed measured inspections of the adult fishway system.

Fish Ladder:  All criteria were met with the exception of the diffuser 14 reading which was at 727.9 feet on the July 9-11 inspections (0.1 feet below criteria).

Fishway Entrances and Collection Channel:  Problems developed with the weir motor and cable control system on north shore fishway entrance number 1 (NSE-1) on the morning of May 31.  Inspection revealed that the cable had broken and the weir gate had dropped to the sill.  The weir motor was also burned up.  A temporary adjustment was done on the weir gate by crane on June 7 and the gate was dogged off at 635.0 feet via cables.  This setting will be maintained until an A-frame and chain hoist system can be put in place to adjust the weir depth relative to the tailwater elevation.  Head differential readings remained within criteria during all fishway inspections this week. Weir depths at the south shore fishway entrances remained within criteria on all inspections. Both north powerhouse fishway entrances were on sill during the week due to tailwater elevations below 636.0 feet (these gates bottom out at elevations below 636.0 feet). Weir depths at the north powerhouse entrances ranged from 6.5 to 7.1 feet.  Weir depths at the north shore fishway entrances were out of criteria on all inspections this week.  The readings on NSE-1 were off the scale (due to the temporary cable fix) while the readings on NSE-2 remained stable on all inspections at 5.1 feet (criteria ≥ 7.0 feet).  Velocity readings in the adult fishway collection channel transition pool area ranged from 0.73 to 0.96 feet per second and averaged 0.84 feet per second.

### Auxiliary Water Supply System:  There were no problems with the auxiliary water system during the report week.   Fish pumps one and two were satisfactorily run all week.  Fish pump 3 remains in standby, ready for service.

#### Juvenile Fish Passage Facility

The juvenile fish facility sample rate remained at the 10.0% level during the report week.

Forebay Debris/Gatewell Debris/Oil:  The amount of forebay debris varied during the week due to wind strength and direction; none was removed.

ESBSs/VBSs:  The last VBS/ESBS video inspections were attempted on June 24-25.  They were cancelled due to near zero water visibility and concerns with the increased spill levels (due to the need to shut off units one at a time) increasing dissolved gas levels.  The next inspections have been moved up to August 5-7.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  Juvenile fish collection gallery orifices were backflushed at regular 3 hour intervals all week.  Vegetative debris levels remained fairly high this report week.  Early on the morning of July 8, the separator bypass valve was partially opened to help move debris off the separator inclined screen. On occasions of partial clogs the separator technicians were able to clear the screen with the power air rake tool that the maintenance staff developed.

Transportation Facility:  The fish transportation facility operated well during the week despite debris issues.  Raceways were swept prior to barge loading and a considerable amount of vegetative material (mainly Elodea) removed.  The facility has continued utilizing the larger (lamprey friendly) mesh raceway tailscreens.

Transport Summary:   Direct loading operations did not take during the report week due to high river flows making overnight loading operations hazardous.  Every other day fish barging proceeded according to schedule on the even numbered days of the report week.  Operations went smoothly all week.

Removable Spillway Weir:  The RSW operated normally as part of the spill plan.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Granite Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 122.8 | 89.5 | 34.0 | 18.5 | 62.6 | 61.7 | 3.6 | 3.0 |

*Scrollcase temperature

Other

Inlined Cooling Water Strainers:  Cooling water strainers were last inspected for lamprey entrainment on June 27.  A total of 38 lamprey were found in the strainers over a combined run time of 3998.6 unit hours.  Unit 6 strainers were not inspected due to a B.P.A. request.  The next inspections are scheduled for July 27-28.

Invasive Species:  The zebra mussel traps near the adult fishway exit were examined for zebra mussels on the July 11 inspection.  No evidence of zebra mussels was found.

Fish Salvage Operation:  A fish salvage operation took place in the draft tube of turbine unit 6 on July 13 between 0800 and 1020 hours.  The following fish were removed alive and returned to the river:  two white sturgeon (approximately 3 and 4 feet in length), one adult smallmouth bass, one adult bridge-lip sucker, 123 adult channel catfish.  Both sturgeon and the first few baskets of catfish were transferred to a pickup-mounted fish tank and released at Offield Landing (above Lower Granite Dam).  All remaining fish were released directly into the tailrace area below the dam.  All fish were released alive with the exception of two channel catfish mortalities which were found when the salvage crew entered the draft tube area.

Research:  Adult fish trap operations continued with a sample rate of 10%.  Scale samples are being taken from one out of every 20 hatchery steelhead.  All wild steelhead and chinook captured are being PIT-tagged and scale and genetic samples taken.  Previously PIT-tagged steelhead or chinook (either hatchery or wild) had both scale and genetic samples taken for verification purposes.  Scale samples are also being taken from one out of every three hatchery chinook.  Sort by code Lemhi origin chinook are being radio-tagged and scale and genetic samples taken.