U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

#### FISH FACILITIES WEEKLY REPORT

#31 - 2011

# Project: McNary

# Biologists: Carl Dugger and Bobby Johnson

Dates: September 23 - 29, 2011

## Turbine Operation

McNary had 11 to 12 units available for power generation this week.  Units 1 and 10 remain out of service for the rewind contract which will be completed in approximately six months to one year.  On September 23, unit 8 returned to service from annual maintenance.  On September 26, unit 9 was removed from service for annual maintenance which will require approximately two weeks to complete.  On September 27, units 2 through 4 were out of service a total of 1.1 hours for ESBS camera inspections.  On September 28, power to the spill gates was interrupted for approximately 30 minutes in support of back up diesel system tests.  For approximately 10 minutes, four spill gates were raised using the diesel system.

The hard constraint one percent criterion continues with no units running outside the criteria.

## Adult Fish Passage Facilities

On September 24, 26 and 29, the McNary fisheries biologist performed measured inspections of the adult fishways.  Adult fish counts continued.  Video review for lamprey counts and the nightly lowering of Oregon entrance weirs, NFEW2, NFEW3, SFEW1 and SFEW2, for lamprey passage will conclude September 30.

Fish Ladders:  Except on September 24, both ladders met all Fish Passage Plan criteria.  On September 24, Washington and Oregon count station differentials measured 0.7 and 1.0 feet, respectively.  Both sets of leads were cleaned by the fisheries staff and the general maintenance crew, in that order.  For most of the week, the leads in both ladders were cleaned daily.  Milfoil continues to be a problem in both ladders.  Woody debris is also affecting the Oregon ladder.  Late in the week, a log boom was put across the Oregon exit in hopes of reducing the amount of woody debris entering the ladder.

On September 28, the power outage in support of the above mentioned spill gate tests caused multiple alarms at the Washington ladder exit.  These alarms were cleared when the power returned.

At the Oregon exit, measured differential readings revealed no problems with the traveling screens.  However, trash rack differential did measure 0.6 feet.  This location continues to be closely monitored.  On September 29, the general maintenance crew noted during cleaning activities that two of the downstream leads though functional have significantly deteriorated.  Project personnel are planning the replacement or repair of these leads during the upcoming winter ladder outage.

Fishway Entrances and Collection Channel:  The Washington ladder was in criteria all week.  Although the technical staff calibrated the Washington ladder entrances, W2 and W3, this week, the LEDs remain out of service.  Cable drum indicators are being used for weir depth measurements.

On September 24 and 26, the Oregon ladder’s north powerhouse entrances, NFEW3, measured 8.9 feet.  The north pool differential measured 0.9 feet on September 24.  Finally, on September 26, entrance weir, NFEW2, measured 8.9 feet.  All other Oregon ladder inspection points were in criteria.  The technical staff will be checking calibration at the Oregon entrances in the near future.  The south powerhouse entrance weir LED at SFEW2 remains out of service.  The weir cable drum dial indicator continues to be used for weir depth measurements.  Collection channel velocities averaged 1.1 feet per second.

Auxiliary Water Supply System:  For the week, fish pumps 1 and 3 were in service with blade angles of approximately 30 degrees with no interruptions in service.  Pump 2 remains out of service for a major overhaul.  The estimated the return to service date is January 31, 2012.

The juvenile facility continued to supply the usual 450 cfs to the north powerhouse pool with no interruptions in service.

The Wasco County PUD turbine unit had no interruptions in service this week.  Even though this turbine unit has not tripped off line recently and the Washington ladder remains in criteria, the project is concerned about the auxiliary water supply as trash racks associated with conduits 3 and 4 require further cleaning.

#### Juvenile Fish Passage Facility

Collection for truck transport continued without incident.  Collection will conclude at 0700 hours on September 30.

For the report week, 20,900 smolts were transported and 329 juvenile lamprey were enumerated.  In addition 34,000 juvenile shad were collected.

Forebay Debris/Gatewell Debris/Oil:  Forebay debris remained light with milfoil being an issue at the facility and at the Washington exit.  Woody debris along with milfoil at the Oregon exit continues to be a concern.

Trash rack differential monitoring revealed no significant problems and no racks were cleaned.  Repairs to the damaged trash rack hoist and cleaning rake continue.

No problems were seen in the gatewell slots.  The slot at 1B remains dewatered.

ESBSs/VBSs:  ESBSs are deployed in all units except in 1A, 1B and 10B slots.  The screens 3B, 5B and 13A slots remain in transducer bypass mode.  On September 28, inspectors noted that the cycle count for the screen at 2B slot had been reset but no reason for this change had been recorded.  On September 27, ESBS camera inspections at units 2 through 4 produced satisfactory results.  The screen in 4C slot was not examined due to a spare ESBS being stored there.  This week, two more screens were taken to the yard for additional rehabilitation.

VBS monitoring revealed no screens out of criteria.  However, on September 26 and 29, nine screens were cleaned as a preventative measure.  Units 1 and 10 are missing three and one VBS(s) respectively.  Screen rehabilitation has been accelerated.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  Forty two orifices were utilized this week and no blockages were observed.  Orifices in 1B and 1C slots remain closed with “make up” orifices opened in 2A and 2B slots.

All system operated well in automatic mode.  The rectangular screen air bubbling system sequencer continues to function but the sequence is not always in order.  On September 29, the technical staff looked into the problem.  Because of this issue, the rectangular screen cleaning device was set to run every 45 minutes for most of the week.  The bubbler and collection channel and bubbler were checked each night at midnight.  No additional problems were found.  The collection channel continues to be routinely monitored during daily checks and during VBS cleaning operations.

Transportation Facility:  Collection for truck transport and daily smolt monitoring continued.  All PIT and sample systems were operational with no problems to report.  From September 24 at 0700 hours to September 25 at 0150 hours, one of the B side counters was inadvertently turned off.  Due to relatively low fish numbers, this had little or no adverse effect.

Transport Summary:  On September 23, 24, 26 and 28, the fish truck successfully completed trips without any difficulties.  An extra trip occurred on September 23, due to the increased numbers of smolts and juvenile shad in the collection.

River Conditions

River conditions during the week are outlined in Table 1 as provided by the smolt monitoring staff whose data day runs from 0700 to 0700 hours.  Clarity data was provided by the control room.  Spill occurred on September 28 to test the diesel back up system as described above.  However, due to the short duration of the test, the spill flow does not appear in the table.  Installation of new spill gate controls continued.

Table 1.  River conditions at McNary Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 113.6 | 98.9 | 0.0 | 0.0 | 66.5 | 65.2 | 6.0 | 5.8 |

Other

Inline Cooling Water Strainers: The next examination will occur in mid-October.

Invasive Species:  The next zebra mussel station examination will occur in early October.

Predatory Bird Observations:  Bird counts continue with the forebay area being checked once a day and the tailwater area being checked twice a day.  Generally, bird numbers appear to be decreasing.  In the tailwater area, high counts were 102 gulls and 59 cormorants.  Most birds were roosting near the spill basin though some activity has been noted at the powerhouse.  This may be due to the out migration of juvenile shad.  Birds were noted passing near the bypass outfalls while feeding in the powerhouse flow.  The water cannon operated well.

The forebay high count included 11 juvenile gulls along with an occasional cormorant.  During ladder inspections, only an occasional small group of gulls or cormorants was noted.  No grebes were seen on project.

Research:  The adult lamprey passage study is in progress.  This study will conclude on September 30.

Project:  Ice Harbor

Biologist: Mark Plummer

Biological Technician: Stephen Jeffers

Dates: September 23 - 29, 2011

## Turbine Operation

Turbine units 1, 2, 4, and 6 were available for operation this reporting period.  Turbine unit 2 went out of service for annual maintenance September 26 at 0843 hours.  Turbine units 3 and 5 remained out of service.  Turbine units 4 and 6 were out of service for a short period September 27 while STS inspections were performed.

## Adult Fish Passage Facilities

### Fish facility personnel inspected the adult and juvenile fish passage ways September 26, 27, 28, and 29.

### Fish Ladders:  All north and south adult fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria.  The adult collection channel velocity is within criteria.

### Fishway Entrances and Collection Channel (inspection date order):  The south shore entrance (SFE) was on sill with a depth of 8.1 feet, on sill with a depth of 8.1 feet, off sill with a depth of 8.0 feet, and on sill with a depth of 8.1 feet.  The north powerhouse entrance (NFE) was on sill with a depth of 7.9 feet, on sill with a depth of 8.1 feet, off sill with a depth of 8.7 feet, and on sill with a depth of 8.0 feet.  The north shore entrance (NSE) was off sill with a depth of 8.3 feet, off sill with a depth of 7.4 feet, off sill with a depth of 7.5 feet, and off sill with a depth of 7.4 feet.  Fishway entrance criterion is 8 feet depth, greater than 8 feet depth, or on sill.  The powerhouse shift operator was notified to make adjustments to the north shore fishway entrance September 27, 28, and 29.  The adult fishway computer was indicating the depths were in criteria.  A trouble report has been initiated to check the calibration of the fish entrance mechanical depth indicator.  All channel/tailwater differentials were in criteria.  Channel/tailwater differential criteria are 1 – 2 feet.

### Auxiliary Water Supply System:  Normally, 2 of the 3 north shore fish pumps are operated.  All north shore fish pumps were available for operation.  South fish pump 3 remains out of service due to vibration issues at the gearbox shaft, repairs are ongoing. The return to service of south fish pump 3 is scheduled for next week.  Currently, 6 of 8 south shore fish pumps are operating.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  No problems to report.  Fish ladder exits are clear of debris and the bubblers are operating.

STSs/VBSs:  STS rotations are in cycle run mode as the average length of both subyearling Chinook and sockeye is above 120 mm at Lower Monumental Dam.  September STS inspections were completed September 27.  A rip in the STS screen mesh was found in gatewell 3-A slot.  The screen was raised for repairs and the turbine unit was taken out of service.   Screen repair or replacement will take place before the turbine unit is returned to service.

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe:   The juvenile fish bypass is in operation.  Twenty orifices are open.

Juvenile Bypass Facility:  The bypass was put into operation March 23.

Fish Sampling:  Fish sampling for the 2011 season concluded July 7.

Removable Spillway Weir:  The RSW is not in operation.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Ice Harbor Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 32.8 | 20.9 | 0.0 | 0.0 | 67 | 66 | 7.1 | 6.5 |

*Unit 1 scrollcase temperature.

Other

Inline Cooling Water Strainers:  Main turbine unit cooling water strainer inspections for September were completed September 27.  No lampreys were found.

Invasive Species: No zebra mussels were observed during this period.

Spill for fish begin April 3, 2011 and ended September 1, 2011.

# Project:  Lower Monumental Dam

# Biologists:  William Spurgeon and Elizabeth Lindsey

Dates: September 23 - 29, 2011

## Turbine Operation

The units are being operated in hard constraint of the 1% operation criteria.  Unit 4 was taken out of service for annual maintenance at 0903 hours on September 12.  The unit was returned to service at 1324 hours on September 29.  Unit 6 was taken out of service at 1511 hours on September 23 due to a thrust bearing oil pump pressure gauge failure.  The unit was returned to service at 0955 hours on September 29.

Adult Fish Passage Facility

The adult fishway was inspected by Corps and PSMFC biologists on September 23, 24, 25, and 28.

Fish Ladders: Fishway exit head differential and depth over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively) on all inspections.  Picketed lead head differential was in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively) on all inspections.

### Fishway Entrances and Collection Channel:  NSE 1 and NSE 2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections.  North shore channel/tailwater head was in criteria (1’-2’) on all inspections.

SPE 1 and SPE 2 weir gates were in sill criteria (criteria: > 8’ or on sill) on all inspections.  While on sill, the gate depth readings were 6.5’, 7.5’, 7.5’, and 7.2 feet.  South powerhouse channel/tailwater head was in criteria (1’-2’) on all inspections.

SSE1 weir gate was in depth or sill criteria (criteria: > 8’ or on sill) on all inspections.  While on sill, the gate depth readings were 7.4’, and 7.8 feet.   SSE 2 was out of criteria (6’ above sill) on all inspections.  SSE 2 was taken out of service on September 15 due to a blown gearbox seal.  The gate is closed pending part procurement and repair.  South shore channel/tailwater head was in criteria (1’-2’) this week.

### Auxiliary Water Supply System: All pumps were in service and operating during this period.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 143.0 square yards of forebay debris observed during this period.  Gatewell debris ranged from 0-24% surface coverage.  No oil was observed in gatewells.

STSs/VBSs:  STSs are operating in cycle mode.  STS inspections of units 1, 2, 4, and 6 were conducted on September 7.  Inspection of unit 4 STS’s revealed the screen in gatewell slot 4C required repair.  The screen was replaced September 8.  All other screens were in good operating condition.   STSs associated with unit 3 and slot 5C were inspected on September 12.  Screens in slots 5A and 5B were inspected on September 19.  These screens were also in good operating condition.

Orifices, Collection Channel, Dewatering Structure, Flume:  The collection channel is operating with 19 orifices open.

Collection Facility:  Facility mortality exceeded 6% on September 23, 24, 25, 26, 27, 28, and 29 due to high incidence of Columnaris.  Percent mortality was 14.0, 21.3, 21.8, 27.4, 24.4, 25.9, and 10.9, respectively.  The percent of sample with columnaris on the days listed above, tracked the mortality rate to within a percentage point.  As is the standard procedure at this facility, the transport tank is treated with salt on every load to ease fungal and bacterial infection. No other problems occurred this week.

Transport Summary:  Transport was changed from alternate day to daily mini/midi-tanker trucking on September 22 in response to increased mortality rates.  This change in operation reduced holding time and stress, and may increase fish survival.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Monumental Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF)* |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 32.9 | 20.4 | 0.0 | 0.0 | 67.0 | 66.5 | 5.0 | 4.3 |

*Scrollcase temperatures.

#### Other

Inline Cooling Water Strainers: Cooling water strainers were inspected on August 9.  No live lamprey was recovered.  Mortalities included 1 lamprey and 180 Siberian prawns.

Invasive Species: There were no zebra mussels observed at the monitoring stations on September 2.

Pelican presence at the bypass outfall has been infrequent.

Project:  Little Goose

# Biologists: Richard Weis

Dates: September 23 - 29, 2011

## Turbine Operation

All units were available for service throughout most of the report period. Turbine unit 2 and 5 were placed out of service on September 29.  Except during scheduled turbine unit validation tests, all turbine operations were within 1% of best efficiency.

## Adult Fish Passage Facility

COE and ODFW fisheries biologists performed measured inspections of the adult fishway on September 23, 25, 27 and 29.

Fish Ladder:  The ladder exit head differentials ranged from 0.0 to 0.2 feet (criteria < 0.5 ft.).  Water depths over the weirs ranged between 0.8 and 2.1 feet (criteria 1.0-1.3 ft.) and picketed lead head differentials ranged between 0 and 0.1 feet (criteria < 0.3 ft.).  No debris was observed at the picketed leads or at the ladder exit.  The air bubbler used to prevent debris from collecting near the ladder exit operated satisfactorily.

Fishway Entrances and Collection Channel:  Channel to tailwater head differentials ranged between 0.8 and 2.1 feet (criteria 1.0 to 2.0 ft.).  SSE weir depths ranged between 8.28 and 8.54 feet (criteria ≥8.0 ft), NPE weirs depths ranged between 6.90 feet (sill) and 7.38 feet (criteria ≥7.0 ft or on sill).  NSE weirs remain at fixed elevations of 531.5 feet and depths ranged between 7.50 and 8.10 feet (criteria ≥ 6.0 ft.).  Collection channel surface water velocities (criteria 1.5 fps) ranged from 1.9 to 2.2 fps near the SSE and 2.0 to 2.9 fps near the NSE.

Auxiliary Water Supply System:  All fish pumps operated in criteria.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:   Estimates of Forebay debris ranged from 120 to 1900 square feet inside the trash/shear boom.

Spillway Weir:  The spillway weir was removed from service on September 1.

ESBS/VBS:   All ESBSs operated within criteria this report period.

Orifices, Collection Channel, Dewatering Structure, and Flume:  The juvenile collection system operated in criteria, with 19 open orifices.

Transportation Facility:  A total 890 Salmonid smolts were collected this report period.   All fish were transported except for mortalities.  Descaling and mortality rates for this report period are 1.1 % and 3.9 % respectively.  Many sample mortalities exhibited signs of presumed Columnaris and BKD disease.

Four adult Pacific Lampreys were recovered from the collection this week and were transported one mile upstream above the dam and released back to river in good condition.

Transport Summary:  Fish were transported on alternate days.  Salt in small concentrations of approximately 1 g/L is added to the midi-tank water to treat potential Columnaris disease and reduce stress.  All transport operations were successfully performed.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1:  River conditions at Little Goose Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 35.1 | 28.8 | 0 | 0 | 67.1 | 66.2 | 6.0+ | 5.0 |

*Ladder temperature.

Other

Inline Cooling Water Strainers:  Cooling water strainers on all units were last inspected on September 28.  No fish were found.

Invasive Species:  The zebra mussel substrate monitor was inspected on September 15.  No mussels were observed.  The next inspection is scheduled for October 10.

Avian Activity:  Up to 24 gulls and 3 cormorants were observed in the vicinity of the dam this reporting period.

Project:  Lower Granite

# Biologists:  Mike Halter and Ches Brooks

Dates: September 23 - 29, 2011

## Turbine Operation

Lower Granite had turbine units 1, 2, and 5 available for power generation at the beginning of the report week.  Turbine unit 6 returned to service at 1832 hours on September 29 and is undergoing exciter testing.  Turbine unit 3 is out of service for cavitation repair.  The tentative return to service date for this unit is December 2.  Turbine unit 4 is out of service for exciter rehabilitation and cooling water strainer replacement.  The tentative return to service date for this unit is October 13.   Mandatory court-ordered spill and minimum operating pool conditions ceased at 0001 hours on September 1.  The Lower Granite forebay operating range was increased to 735.0 – 736.0 feet as a soft constraint, and 735.0 – 738.0 as a hard constraint.

## Adult Fish Passage Facility

On September 24, 27, and 28 the Lower Granite COE and PSMFC fisheries biologists performed measured inspections of the adult fishway system.

Fish Ladder:  All criteria were met.

Fishway Entrances and Collection Channel:  Head differential readings at all fishway entrances remained within criteria during the fishway inspections this week with the exception of the September 27 inspection when the north shore entrance had a reading of 0.7 feet (criterion 1.0 – 2.0 feet).  Weir depths at the south shore fishway entrances also met criteria during the weekly inspections.  Weir depths at the north powerhouse entrance were on sill during the September 24 inspection due to low tailwater elevations (these weirs bottom out at 636.0 feet).  On subsequent inspections higher tailrace levels allowed these gates to meet depth criteria (criterion ≥ 8.0 feet).  Weir depths measurements at the north shore entrances produced mixed results.  Weir depths at entrance NSE 1 met criteria on the September 27 and 28 inspections, but were below criteria on the September 24 inspection. Weir depths at the NSE 2 gate entrance were below the desired range for the duration of the week with readings ranging from 4.9 to 5.4 feet (criterion ≥ 7.0 feet).  Velocity readings in the adult fishway collection channel transition pool area ranged from 0.78 to 1.03 feet per second and averaged 0.93 feet per second.

### Auxiliary Water Supply System:  There were no problems with the auxiliary water system during the report week.

#### Juvenile Fish Passage Facility

The juvenile fish facility sample rate started at 50% this report week.  On September 25 at 0700 hours the sample rate was increased to 100% due to decreased fish numbers.  Fish are being processed in the lab every other day (even days of the month during September).  Additional separator bars with a smaller spacing were fitted over the top of the existing separator bars on the morning of September 26 to prevent mini-jack Chinook from falling through the regular bars and ending up in the sample.

Forebay Debris/Gatewell Debris/Oil:  The amount of forebay debris varied during the week due to wind strength and direction; none was removed.

ESBSs/VBSs:  VBS/ESBS video inspections last took place on August 6 - 7.  The inspector noted that an approximately 3 foot section of VBS retaining strap was missing in gatewell slot 1-B.  He also noted that the mesh was entirely in place. This section will be closely monitored in upcoming inspections and repaired during winter maintenance.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  Juvenile fish collection gallery orifices were backflushed at regular 3 hour intervals all week.  Debris levels remained light.  It was not necessary to enter primary bypass mode to clean the inclined screen during this week.

Transportation Facility:  Sample fish were processed and transported every other day.  NOAA-Fisheries personnel PIT-tagged subyearling Chinook in the lab to evaluate late season truck transport operations from Lower Granite.  The downstream raceways are being utilized for fish loading when fish numbers warrant.

Transport Summary:   Truck transport of fish is taking place on even numbered days of the month in September.  The semi truck was utilized all this week, except for the September 26 trip when the midi-tanker was used.  Trucked fish are being released into the Bonneville bypass line.   All transport operations went smoothly and according to schedule.

Removable Spillway Weir:  Nothing to report.  Spill operations have concluded for the season.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Granite Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 37.4 | 29.7 | 0.0 | 0.0 | 67.6 | 67.3 | 4.8 | 4.3 |

*Scrollcase temperature

Other

Inline Cooling Water Strainers:   Cooling water strainer inspections were conducted on September 20.  The strainers in units 1, 2, 5, and 6 were inspected (unit 3 was out of service for cavitation repair; unit 4 was out of service for exciter rehab and strainer replacement; unit 6 is undergoing exciter rehab).  No lamprey were found this month over a total run time of 1,261.7 hours.

Invasive Species:  The zebra mussel traps near the adult fishway exit were last examined for zebra mussels on the September 4 inspection.  No evidence of zebra mussels was found.

Research:  Adult fish trap operations continued during the week with a sample rate of 10%.  Scale samples are being taken from one out of every 25 hatchery steelhead.  All wild steelhead captured are being PIT-tagged and scale and genetic samples taken.  Any previously PIT-tagged steelhead (either hatchery or wild) will have both scale and genetic samples taken for verification purposes.  Scale samples are also being taken from one out of every three wild fall Chinook.  Scale samples are also being taken from NOAA-Fisheries PIT-tagged Chinook.

NOAA-Fisheries personnel continued PIT-tagging subyearling Chinook for the late season truck transport evaluation study.  Fish are being taken directly from the JFF lab sample. Tagging operations for this study will continue through the duration of fall transport.

Fall Chinook Transport:   Collection of adult fall Chinook for transport to Lyons Ferry Hatchery and the Nez Perce Hatchery at Cherry Lane continued during the week.   Trucking operations will continue into November (or until hatchery needs are met).