U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

#### FISH FACILITIES WEEKLY REPORT

#38 - 2011

# Project: McNary

# Biologists: Carl Dugger and Bobby Johnson

Dates: November 11 - 17, 2011

## Turbine Operation

McNary had 9 to 11 units available for power generation this week.  See Table 1 for a breakdown of outages.

Table 1.  Units Available for Power Generation

| Unit Number | Dates down | Reason | Return to Service* |
| --- | --- | --- | --- |
| 1, 10 | All week | Rewind contract | 1/2012* |
| 7 | All week | Unit overhaul | 12/20/11* |
| 9 | 11/11 – 11/17 | Relay replacement | 11/17/11 |
| 5 | 11/14 – 11/15 | Failed ESBS, B Slot | 11/15/11 |
| 13 | 11/15 | Failed ESBS, C Slot | 11/15/11 |
| 6,8,11,12 | 11/14 – 11/17 | Dive: Hydro-acoustic installation | 11/17/11 |

*Indicates expected return to service date.

On November 1, when the soft constraint one percent criterion began, the project operated the units outside the one percent soft constraint during the outages for the diving contract, listed in Table 1, and to meet BPA requests.  From November 10 to 15 the project reduced Unit 5’s load to the lower end of the criteria due to a high VBS differential in Slot 5B.  The debris sloughed off and the project increased the load, but crews cleaned the screen after a high differential reading on November 16.  On November 15 the project reduced the loads on Units 3 and 11, and on November 16, Unit 4, until crews could clean the respective VBSs.

## Adult Fish Passage Facilities

On November 12, 14 and 16, the McNary fisheries staff inspected the adult fishways.

Fish Ladders:  During these measured inspections, both ladders met all Fish Passage Plan criteria.  At the Washington exit, Weir 335’s alarm sounded once and control room personnel reset it.  At the Oregon exit, the traveling screens’ alarm sounded once and control room personnel reset it.  There were no problems with the screen or trash rack differential readings.

Fishway Entrances and Collection Channel:  The Washington ladder was in criteria all week.  On November 16, crews installed a new hoist motor on entrance weir W3 and returned it to automatic operation.

For the week, the Oregon ladder’s north powerhouse entrance weirs, NFEW2 and NFEW3, measured depths ranging from 8.7 to 8.8 feet.  Staff again noted slack in the hoist cables for NFEW2, possibly due to roller problems.  The project will repair the rollers this winter.

All other Oregon ladder inspection points were in criteria.  Crews have not yet replaced the failed LED on the south powerhouse entrance weir, SFEW2.  Until then, staff will use the dial indicator on the weir’s cable drum for measurements.  The collection channel velocity averaged approximately 1.2 feet per second.

Auxiliary Water Supply System:  For the week, fish pumps 1 and 3 were in service with blade angles of approximately 30 degrees with no recorded interruptions.  Pump 2 remains out of operation due for major overhaul.  The project plans to contract out this work.

The juvenile facility continues to supply the usual 450 cfs to the north powerhouse pool, with no interruptions in service.  However, on November 18, when crews switch the juvenile system to emergency bypass, this auxiliary water will no longer be available.

Finally, the Wasco county PUD had no interruptions in service this week.  The project remains concerned about the auxiliary water supply, because the trash racks at Conduits 3 and 4 still require further cleaning.

#### Juvenile Fish Passage Facility

Fall primary bypass season continues with light maintenance occurring at the facility.  However, due to the failure of the rectangular screen cleaning device, discussed below, facility personnel will switch the system to emergency bypass on November 18 in order to repair the mechanism.

Work continues on the facility’s new bypass outfall, which the contractor should complete before next season.  On November 13 one of the core drilling barges broke loose and drifted down river.  The contractor retrieved the barge with no apparent problems.

Forebay Debris/Gatewell Debris/Oil:  During the week, forebay debris remained light but the quantity did increase.  After last week’s storms, there were more leaves and milfoil suspended in the water.  Trash rack differentials were acceptable and crews did not clean any racks.  Crews continued repairing the damaged trash rack hoist and cleaning rake.  Facility personnel did not encounter any problems in the gatewell slots.

ESBSs/VBSs:  ESBSs are installed at all units except units 1 and 10.  The screens in slots 2A, 3B, 11A, 11B, 11C, 13A and 13B remain in transducer bypass mode.  The screen in slot 5B was already in transducer bypass mode before crews replaced it.  The screen in slot 13C also failed and crews replaced it, as mentioned above.  Staff completed camera inspections in units 5, 6 and 8 while these units were out of service for the dive contract work.  On November 14, staff found a failed screen at slot 5B.  There was no previous indication of the failure and on October 4, during the last camera inspection, the screen brush bar was operational.  ESBS rehabilitation continues.  On November 16, due to increased debris, staff changed brush cycles from 60 to 45 minutes.

VBS monitoring revealed 18 screens out of criteria while the units were operating at 79 megawatts.  Crews cleaned these screens along with the screen at slot 5B, which had measured high differentials last week.  Crews cleaned 11 other screens as a preventative measure.  There are no VBSs in Slots 1B, 1C and 10A as these turbine units are out of service.  Crews continue to rehabilitate screens.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  The project operated 42 orifices this week.  On November 16, while unit 4 was out of service, the general maintenance crew removed woody debris from slot 4B, with no apparent harm to fish.  That same day staff reopened the orifice at slot 1A and closed the make-up orifice.

All systems operated well in automatic mode except as described here:  On November 16, staff set the rectangular and side screen cleaning brush cycles at 30 and 90 minutes, respectively, due to increased debris.  Later that day, the rectangular screen mechanism suffered a mechanical failure.  The maintenance crews will be forced to switch the facility from primary bypass to emergency bypass mode in order to access the screen mechanism and conduct the repairs.

On November 17 staff prepared the channel and the facility for the switch to emergency bypass operations.  The switch will occur on November 18 and will include winterizing the facility, with the whole process taking eight to ten hours.  Until the switch is made the fisheries staff will “camp” in the channel and run the air burst system as needed.  The transition screen cleaning device remains out of service.  Staff also monitored the channel during VBS cleaning.

Due to the dewatering of Station Service unit 01, the collection channel drain chamber filling water and transport line flush flow will not be available until approximately December 12, when the unit returns to service.

Update: On November 19, crews found a failed key for the brake/clutch, and replaced it (after the close of this report period) .

Transportation Facility:  Fall bypass season and light maintenance continues.  All systems remain off.  The facility will remain watered to avoid freeze breakage until crews switch to emergency bypass on November 18.  Crews continue to build lamprey-friendly raceway tailscreens.

Transport Summary:  The transport season ended September 30.

River Conditions

The Control Room provided river conditions during the week, as outlined in Table 2, with each data day running from 0000 to 2400 hours.  On November 16, due to flow in excess of powerhouse capacity, the project spilled the scheduled 20 to 35 kcfs excess flow from 0744 to 1634 hours.  A contractor continues to rehabilitate the TSWs.

Table 2.  River conditions at McNary Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 149.1 | 113.8 | 13.1 | 0.0 | 53 | 50 | 6.0 | 6.0 |

Other

Inline Cooling Water Strainers: On November 22, crews will examine the cooling water strainers.

Invasive Species:  Staff will examine the zebra mussel stations in early December.

Predatory Bird Observations:  We are no longer counting birds.  During casual observations, bird numbers appear to be fluctuating with juvenile shad out migration numbers.  There were gulls, mergansers and cormorants in the tailwater area.  Most cormorants roosted near the spill basin, while the gulls frequented the powerhouse flow area.  The mergansers rafted by the south edge of the spill basin.  Gulls and cormorants fed there during the spill.  Some cormorants, mergansers and gulls occasionally fed at the bypass outfalls.  The water cannon operated well.  On November 16, the sprinkler head jammed on debris or ice, but later cleared itself.

In the forebay area staff noted an occasional gull, cormorant or grebe.  While inspecting fish ladders, staff observed groups of gulls roosting along the Washington shore.

Research:  No research is currently underway.  However, contractors continue preparations for the juvenile survival and the adult fallback studies.  Dive contractors will install equipment for both studies in November and December.

Project:  Ice Harbor

Biologist: Mark Plummer

Biological Technician: Stephen Jeffers

Dates: November 11 - 17, 2011

## Turbine Operation

Turbine units 1, 2, and 4 were available for operation this reporting period.  Turbine 2 was out of service for a short period November 14 to perform STS and cooling water strainer inspections.  Turbine units 1 and 4 were out of service for short periods November 16 to perform STS and cooling water strainer inspections. Turbine unit 3 remains out of service for rotor pole repair.  Turbine unit 5 remains out of service for breaker repairs.  Turbine unit 6 remains out of service for annual maintenance.

## Adult Fish Passage Facilities

### Fish facility personnel inspected the adult and juvenile fish passageways November 15 and 16.

### Fish Ladders:  All north and south adult fish ladder inspection areas (picketed leads, head differentials, fishway exits, depth over weirs, and adult fish collection channel velocity) were within criteria.  The north and south fish ladder picketed leads are raised.

### Fishway Entrances and Collection Channel (inspection date order):  The south shore entrance (SFE) was off sill with a depth of 8.2 feet and on sill with 8.2 feet.  The north powerhouse entrance (NFE) was off sill with a depth of 8.2 feet and off sill with 6.7 feet.  The north shore entrance (NSE) was on sill with a depth of 8.9 feet and on sill with 8.4 feet.  Fishway entrance criterion is 8 feet depth, greater than 8 feet depth, or on sill.  The out of criteria at the SFE November 16 was found to be a problem with the gate limit switches.  Repairs were made and the entrance returned to sill.  All channel/tailwater differentials were in criteria.  Channel/tailwater differential criteria are 1 – 2 feet. Water velocity in the adult south fish collection channel remained in criteria at 1.5 fps – 4.0 fps.

### Auxiliary Water Supply System:  All 3 north shore fish pumps were available for operation, 2 of the 3 north shore fish pumps are operated.  Six of 8 south shore fish pumps are operating.

### South fish pump 3 remains out of service due to vibration issues at the gearbox shaft, repairs are ongoing.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  No problems to report.  Fish ladder exits are clear of debris and the bubblers are operating.  A sheen of oil observed in turbine unit 6 - C slot was reported to the powerhouse shift operator November 16.

STSs/VBSs:  The STS rotations are in cycle run mode. No problems were observed during the November STS/VBS inspections.

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe:   The juvenile fish bypass is in operation for adult fallbacks.  Twenty orifices are open.

Juvenile Bypass Facility:  The bypass was placed into operation March 23.

Fish Sampling:  Fish sampling for the 2011 season concluded July 7.

Removable Spillway Weir:  The RSW is not in operation.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Ice Harbor Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 29.2 | 12.7 | 0.0 | 0.0 | 54 | 51 | 5.8 | 5.8 |

*Unit 1 scrollcase temperature.

Other

Inline Cooling Water Strainers:  No lamprey were observed in the main unit cooling water strainers during November inspections.

Invasive Species:  No zebra mussels were observed during this period.

# Project:  Lower Monumental Dam

# Biologists:  William Spurgeon and Elizabeth Lindsey

Dates: November 11 - 17, 2011

## Turbine Operation

The units are being operated within soft constraint of the 1% operation criteria.  Unit 3 was taken out of service at 0732 hours on October 25 for annual maintenance.

Adult Fish Passage Facility

The adult fishway was inspected by Corps biologists on November 15, 16, and 17.

Fish Ladders:  Fishway exit head differential were within criteria (< 0.5’) during all inspections.  Depths over the weirs were within criteria (1.0’-1.3’) on all inspections.  Picketed lead head differential was in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively) on all inspections.  The adult counting season ended October 31.  North and south ladder picketed leads were raised on November 3 and November 9, respectively.

### Fishway Entrances and Collection Channel:  NSE 1 and NSE 2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections. North shore channel/tailwater head was in criteria (1’-2’) on all inspections.

SPE 1 and SPE 2 weir gates were in sill criteria (criteria: > 8’ or on sill) on all inspections.  While on sill, the gate depth readings were 5.7’, 6.8’, and 6.6 feet.  South powerhouse channel/tailwater head was in criteria (1’-2’) on all inspections.

North shore collection channel velocity was in criteria on all inspections (criteria: 1.5-4.0 ft/s).  The installed velocity meter is not reading accurately which may be due to algal growth on the sensor plate.  A reading was conducted with a portable unit and showed that a 1.3 ft/sec reading on the installed system reads 2.2 ft/s on the portable unit.

SSE1 weir gate was in depth or sill criteria (criteria: > 8’ or on sill) on all inspections.  While on sill, the gate depth readings were 6.7’ and 7.6 feet.   SSE 2 was in criteria (6’ above sill) on all inspections.  South shore channel/tailwater head was in criteria (1’-2’) this week.

### Auxiliary Water Supply System:  All pumps were in service and operating during this period.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 96.7 square yards of forebay debris observed during this period.  Gatewell debris ranged from 0-15% surface coverage.  No oil was observed in gatewells.

STSs/VBSs:  STS’s are operating in cycle mode.  Unit 3 STSs were raised on November 15.

Orifices, Collection Channel, Dewatering Structure, Flume:  The collection channel is operating with 18 orifices open.

Collection Facility:  The load and hold facility is in winter maintenance mode.

Transport Summary:  Transport ended October 1.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Monumental Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF)* |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 30.3 | 15.1 | 0.0 | 0.0 | 51.0 | 50.0 | 4.2 | 3.8 |

*Scrollcase temperatures.

#### Other

Inline Cooling Water Strainers:  Inline cooling water strainers were inspected on November 2.  No live lamprey was recovered.  Mortalities included 12 juvenile shad and 3 Siberian prawns.

Invasive Species:  There were no zebra mussels observed at the monitoring stations on November 3.

Project:  Little Goose

# Biologists: Richard Weis

Dates: November 11 - 17, 2011

## Turbine Operation

All units were available for service throughout the report period except turbine unit 1.  Unit 1 was placed out of service on October 25 for annual maintenance and 6-year overhaul.  All turbine operations were within 1% of best efficiency.

## Adult Fish Passage Facility

COE and ODFW fisheries biologists performed measured inspections of the adult fishway on November 15, 16 and 17.

Fish Ladder:  The ladder exit head differentials ranged from 0 to 0.2 feet (criteria < 0.5 ft.).  Water depths over the weirs ranged between 1.1 and 1.2 feet (criteria 1.0-1.3 ft.) and picketed lead head differentials ranged between 0 and 0.1feet (criteria < 0.3 ft.).  No debris was observed at the picketed leads or the ladder exit.  The air bubbler used to prevent debris from collecting near the ladder exit operated satisfactorily.

Fishway Entrances and Collection Channel:  Channel to tailwater head differentials ranged between 1.2 and 2.0 feet (criteria 1.0 to 2.0 ft.).  SSE weir depths ranged between 8.28 and 8.36 feet (criteria ≥8.0 ft).  NPE weirs depths ranged between 6.56 feet (sill) and 7.20 feet (criteria ≥7.0 ft or on sill).  NSE weirs remain at fixed elevations of 531.5 feet and depths ranged between 7.3 and 8.06 feet (criteria ≥ 6.0 ft.).  Collection channel surface water velocities ranged from 2.1 to 2.3 fps (criteria 1.5-4.0 fps) near the SSE and ranged between 2.3 and 2.5 fps near the NSE.

Auxiliary Water Supply System:  All three fish pumps operated in criteria

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:   Estimates of forebay debris ranged from 200 to 400 square feet inside the trash/shear boom.   Hand removal of debris from gatewells remained steady during this period.

Spillway Weir:  The spillway weir was removed from service on September 1.

ESBS/VBS:   All ESBS operated within criteria this report period.  Drawdown measurements across turbine units 2 and 3 trashracks/ESBS and VBS were conducted on November 15.  All measurements were within normal operating criteria.

Orifices, Collection Channel, Dewatering Structure, and Flume:  The juvenile collection system operated in criteria with 19 open orifices.

Transportation Facility:  The facility was switched to primary by-pass on October 31 at 0700 hours. All fish are routed to the tailrace mid-channel area.  Seasonal maintenance work at the facility is in progress.

Transport Summary:  Fish transport ended on October 31.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1:  River conditions at Little Goose Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 29.5 | 16.7 | 0 | 0 | 49.7 | 48.9 | 5.6 | 5.3 |

*Ladder temperature.

Other

Cooling Water Strainers:  Cooling water strainers on all units were inspected on November 17.  No fish were found.

Invasive Species:  The zebra mussel substrate was inspected on November 8.  No mussels were observed.  The next inspection is scheduled for December 15.

Avian Activity:  Up to 4 gulls were observed in the vicinity of the dam this reporting period.

Project:  Lower Granite

# Biologists:  Mike Halter and Ches Brooks

Dates: November 11 - 17, 2011

## Turbine Operation

Lower Granite had turbine units 1, 2, 4 and 6 available for power generation at the beginning of the report week.  Turbine unit 3 is out of service for cavitation repair.  The tentative return to service date for this unit is December 2.  Turbine unit 5 is out of service for annual maintenance.  The tentative return to service date for this unit is November 30.  Mandatory court-ordered spill and MOP operations ceased at 0001 hours on September 1.  The Lower Granite forebay operating range was increased to 735.0 – 736.0 feet as a soft constraint and 735.0 – 738.0 as a hard constraint.

## Adult Fish Passage Facility

On November 11, 12, 14 and 17 the Lower Granite COE fisheries biologists performed measured inspections of the adult fishway system.

Fish Ladder:  All criteria were met.

Fishway Entrances and Collection Channel:  Head differential readings at all fishway entrances remained within criteria during the fishway inspections this week with the exception of the November 11 inspection when the north shore entrance had a reading of 0.8 feet (criterion 1.0 – 2.0 feet).  Weir depths at the south shore fishway entrances remained within criteria on all inspections this week (criterion ≥ 8.0 feet).  The north powerhouse fishway entrance weir depths were also within criteria on all inspections this week.  Weir depths measurements at the north shore entrances again produced mixed results.  Weir depths at entrance NSE 1 met criteria on all inspections.  Weir depths at the NSE 2 gate entrance were below the desired range all week with readings measuring 5.1 feet (criterion ≥ 7.0 feet).  Velocity readings in the adult fishway collection channel transition pool area ranged from 0.84 to 1.02 feet per second and averaged 0.94 feet per second.

### Auxiliary Water Supply System:  During the report week the auxiliary water system operated with fish pumps 1 and 3 in service.

#### Juvenile Fish Passage Facility

The juvenile fish collection system was operated in the secondary bypass mode (all fish routed back to the river through the mid-river release pipe).  The system is scheduled to operate in that mode through December 15 if weather conditions permit.

Forebay Debris/Gatewell Debris/Oil:  The amount of forebay debris varied during the week due to wind strength and direction; none was removed.

ESBSs/VBSs:  VBS/ESBS video inspections last took place on October 24.  Only unit 5 screens were inspected, the other screens will be inspected as personnel and powerhouse operations permit.  No problems were found with the screens that were inspected.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  Juvenile fish collection gallery orifices were backflushed at regular 3 hour intervals all week.  Debris levels remained light during the week.  It was not necessary to go into bypass mode to clean the inclined screen during this week.

Transportation Facility:  The facility operated in secondary bypass mode (all fish routed back to the river through the mid-river release pipe).  This activity will continue until December 15 (weather permitting).  The separator complex is still being manned 24 hours, 7 days per week due to fish being routed over the separator bars.  No PIT-tag detection system is available at Lower Granite unless fish are diverted through the separator.  Operation of the separator in secondary bypass mode will allow the detection of PIT-tagged juvenile fish (primarily subyearling chinook) to help determine late season movement patterns.

Transport Summary:  All transport operations concluded on November 1.

Removable Spillway Weir:  Nothing to report.  Spill operations have concluded for the season.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Granite Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 28.8 | 18.5 | 0.0 | 0.0 | 51.0 | 49.8 | 5.0 | 5.0 |

*Scrollcase temperature

Other

Inline Cooling Water Strainers:  Duplex strainer inspections for lamprey were last conducted on October 18.  No lamprey were found over a combined run time of 1,259.2 hours.  (Only units 1, 2, and 6 were inspected this time due to the other units being tagged out of service).

Invasive Species:  The zebra mussel traps near the adult fishway exit were examined for zebra mussels on the November 12 inspection.  No evidence of zebra mussels was found.

Research:  Adult fish trap operations continued during the week with a sample rate of 10%.  Scale samples are being taken from one out of every 25 hatchery steelhead.  All wild steelhead captured are being PIT-tagged and scale and genetic samples taken.  Any previously PIT-tagged steelhead (either hatchery or wild) will have both scale and genetic samples taken for verification purposes.  Scale samples are also being taken from one out of every three wild fall Chinook.  Scale samples are also being taken from NOAA-Fisheries PIT-tagged Chinook.  The sampling of adults is scheduled to end on November 20.

Fall Chinook Transport:   Due to a high number of adult females in the run, brood stock goals (for females) have largely been met at Lyons Ferry Hatchery and at the Cherry Lane tribal hatchery.  Trapping operations have stopped at Lyons Ferry Hatchery due to the fact that 75% of the fish being trapped were females.  Protocols at the Lower Granite adult trap were modified and only Chinook females that are wire-tagged (2 out of 3) are being hauled to Lyons Ferry.  In order to increase the number of males available to spawn, the protocol was also changed and untagged males ≥ 65 cm are now being hauled to Lyons Ferry.   The tribal hatchery at Cherry Lane is filling any remaining fish needs by going to Lyons Ferry rather than going directly to Lower Granite.  The final adult transport truck left the adult trap on November 17.