U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

#### FISH FACILITIES WEEKLY REPORT

#01-2012

# Project:  McNary

# Biologists: Carl Dugger and Bobby Johnson

Dates: March 1 - 8, 2012

## Turbine Operation

McNary had 13 turbine units available for power generation this week.  Turbine unit outages are recorded in Table 1.  The project does not know when unit 1 will return to service.

Table 1.  Turbine unit outages at McNary Dam.

| Unit(s) | Outage Dates | Outage Length | Reason |
| --- | --- | --- | --- |
| 1 | All week. | All week. | Oil leak after rewind. |
| 14 | March 1. | 8.9 hours. | Exciter tuning. |
| 2, 3, 4, 5 | March 1. | 4.3, 6.1, 6.1, 1.8 hours. | Contract dive. |
| 2 | March 5. | 5.9 hours. | Unit in and out of service-governor. |
| 6 | March 7. | 4.7 hours. | Tap hub. |

On April 1, the hard constraint one percent criteria will begin.

## Adult Fish Passage Facilities

On March 1, 4, 6 and 7, the McNary fisheries biologist performed measured inspections of the adult fishways.  On February 29, the project lowered the picketed leads so adult fish counting by video monitoring could begin on March 1 at both ladders.  The project repaired and installed Oregon picketed leads.  This winter, a contractor installed new electrical lines at both exits for new cranes scheduled for 2013 installation.

During January, the project inspected and maintained the Oregon ladder above water.  The ladder could not be dewatered due to the exit crane and the 1000 CFS supply intake valve being out of service.  The fisheries staff used a camera to examine the diffuser grating.  Also, the staff video-inspected the entrance weirs for lamprey passage improvements.  In late February, the project installed stilts on SFEW2 for lamprey passage.  The project also repaired one roller on the weir.  On February 29, facility personnel helped install new PIT tag detectors at the Oregon count station.

During February, the project inspected and maintained the Washington ladder.  The ladder could not be completely unwatered to tailwater elevations due entrance bulkheads problems.  Fisheries staff conducted instead a video camera inspection of the diffuser grating.  The fisheries staff also camera inspected the bulkheads for replacement and the entrance weirs for lamprey passage.  The project operated and tested entrance weir W1 and determined that it does run shallower than W2 and W3.

### Fish Ladders:  During measured inspections, both ladders met all Fish Passage Plan criteria except on March 1 and 6 when the Washington ladder’s head over weir measured 0.9 feet.  From February 27 to March 1, the Washington ladder, including the entrance, was in manual mode due to the power being out for electrical upgrades.  After crews completed the work, low water alarms occurred.  On March 6, the biologist asked the operators to adjust the ladder exit weir set points, which resolved the issue.

### On March 7, at the Oregon exit, though in criteria, multiple weir alarms occurred due to encoder issues, which the project resolved.  Electricians also adjusted the set points.  During the winter, the traveling screen wash pump failed, causing the traveling screens to be removed from service.  Also, on March 7, the project installed the repaired pump and returned the screens to service.  Otherwise differential monitoring of the screens during the winter revealed no problems.

Fishway Entrances and Collection Channel:  On the Washington ladder, all inspection points were in criteria except on March 6 and 7 when weir W3, measured depths of 7.5 and 7.8 feet, respectively.  The biologist asked the technical staff to examine the weir as it appears not to be moving.

For the week, on the Oregon ladder, the north powerhouse pool differential measured from 0.7 to 0.8 feet.  North entrance weirs NFEW2 and NFEW3 measured depths of 8.6 to 8.8 feet.  These readings were due to the juvenile facility being out of service and low tailwater elevations.  On March 7, the south pool differential measured 0.9 feet.  This may be due to low tailwater elevation and the stilts on SFEW2.  All other Oregon inspection points were in criteria.  The collection channel velocity averaged 1.5 feet per second.  The project will install a new velocity meter in the near future.

### Auxiliary Water Supply System:  The project maintained fish pumps 1 and 3 during the winter.  For the week, pumps 1 and 3 were in service with blade angles of 30 degrees and no interruptions in service.  Pump 2 remains out of service for major overhaul, which will require a contract.

### Due to issues with the exit crane and intake valve, the 1000 CFS supply conduit remained open all winter.  The juvenile facility is not yet supplying the usual 450 cfs to the north powerhouse pool.

### In February, the Wasco County PUD unit underwent maintenance.  During this time, the project cleaned the conduits’ intake trash racks and examined them with a camera.  The cleaning procedure worked well.  PUD personnel also discovered two loose bypass diffusers.  The project is working with the PUD to reattach the diffusers in the near future.

#### Juvenile Fish Passage Facility

The facility remains shut down for winter maintenance, which is nearing completion.  By March 16, the contractor will test and complete the new primary and secondary bypass lines along with the PIT tag system and adult return lines.  On March 26 or before, the project will test and water up the system for spring bypass season.

Forebay Debris/Gatewell Debris/Oil:  For the week, forebay debris was light but increasing due to the arrival of additional woody debris and tumbleweeds.  During the winter, the fisheries staff monitored trash rack differentials and no problems were seen.  Next week, the project should complete work on the intake deck crane trash hoist, which will permit the resumption of trash rack cleaning can resume.  This week, a slight amount of fish screen oil was observed in six slots which was subsequently removed with absorbent pads.

ESBSs/VBSs:  All ESBSs remain raised and the project has almost concluded maintenance.  Screen rehabilitation continues with the installation of new motors, chains and proximity switches.  The project plans to delay installation of the screens until April 5 to 15, similar to the last three seasons, for juvenile lamprey passage.

In January, the project installed a VBS in slot 1C.  This unit remains out of service.  VBS rehabilitation also continued during the winter.  When ESBS installation begins, fisheries staff will resume VBS differential monitoring.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  The orifices remain closed for winter maintenance, which is near conclusion.  The fisheries staff has fixed the attraction lights, reconditioned the orifice operator oil reservoirs and removed old study equipment.  The project maintained all systems and worked on the issue of water in the orifice air supply line.  In the near future, the project will install a drier in the line.  Air is used to operate the orifice valve actuators.  The project also found that one of the issues with the transition screen cleaning device was water in the air line to the latch pin.  Staff will rewater the channel and resume bypass operations in late March.

Transportation Facility:  The facility remains unwatered for winter maintenance, which is near completion.  The fisheries staff replaced gaskets, rebuilt drive wheels on the east raceway gantry, repaired the porosity unit’s perforated plate and finished building the lamprey friendly raceway tailscreens.  The staff also reconditioned the PIT tag system and sample gates.  The bypass contractor installed an extension on the west raceway drain for juvenile lamprey passage.

Transport Summary:  No fish transport operations are taking place at this time.

River Conditions

River conditions during the week are outlined in Table 2 as provided by control room data, which runs from 0000 to 2400 hours each day.  The project plans to install the rehabilitated TSWs before April 10.  Water temperature measurements are taken from the unit 1 scroll case.

Table 2.  River conditions at McNary Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 162.7 | 109.7 | 0.0 | 0.0 | 40 | 39 | 6.0 | 3.8 |

Other

Inline Cooling Water Strainers:  Examinations in January resulted in seven juvenile lampreys recoveries, six off which were mortalities.  In February, the inspection count was 167 lampreys with 32 mortalities.  Ninety eight live lampreys were found at unit 7.  The fisheries staff observed no salmonids.  The project will examine the main unit cooling water strainers later this month.

Invasive Species:  During winter maintenance, the project observed no invasive species. The biologist will conduct a zebra mussel station examination later this month.

Predatory Bird Observations:  Bird counts will resume later in the month when technicians are on shifts.  Gulls, cormorants, grebes, pelicans and bald eagles appear to over winter in the general area.  This week, in the tailwater area, the biologist observed an occasional gull, pelican or cormorant.  The bypass system is not functional so there are no birds to observe.  In the forebay area, we observed five grebes.

Research:  The adult fallback study continues with other researchers preparing for the juvenile salmonid and adult lamprey passage studies.

Fish Salvage:  On February 8, while salvaging fish from the unit 1 draft tube, the fisheries staff encountered a burbot.

Project:  Ice Harbor

# Biologist:  Mark F. Plummer

Dates: March 1 - 8, 2012

## Turbine Operation

Turbine units 1, 4, and 6 were available for operation this reporting period.  Turbine units 2, 3, and 5 remain out of service due to transformer cooling water problems.  Turbine unit 4 was taken out of service March 8 from 0637 to 1816 hours in support of Doble tests.

## Adult Fish Passage Facilities

### Fish facility personnel inspected the adult fishways March 2, 3, 6, and 8.

### Fish Ladders:  All north and south adult fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria.   The north adult fish ladder was out of service January 28 – February 22 for annual maintenance and improvements for lamprey passage.  This ladder was completely unwatered during this outage.  The south adult fish ladder was out of service January 3 – 26 for annual maintenance and improvements for lamprey passage.  The video inspection of the south lower adult collection channel revealed a section of diffuser grating that was lifted out of position.  Divers were called in to replace the grating and complete the lower ladder visual inspection.  The north and south fish ladder picketed leads are raised.  They will be lowered prior to adult fish counting beginning April 1.  The adult collection channel velocity meter has been replaced and is functioning.

### Fishway Entrances and Collection Channel (inspection date order):  The south shore entrance (SFE) was off sill with a depth of 8.3 feet, off sill with a depth of 8.1 feet, off sill with a depth of 8.2 feet, and off sill with a depth of 8.0 feet.   The north powerhouse entrance (NFE) was off sill with a depth of 8.3 feet, off sill with a depth of 8.2 feet, off sill with a depth of 7.9 feet and off sill with a depth of 7.6 feet.  The north shore entrance (NSE) was off sill with a depth of 8.6 feet, off sill with a depth of 8.3 feet, off sill with a depth of 8.2 feet, and off sill with a depth of 7.8 feet.  Fishway entrance criterion is 8 feet depth, greater than 8 feet depth, or on sill.  The NFE was reported out of criteria to the shift operator.  Adjustments were made with the adult fishway controls to lower the NFE back into criteria.  The NFE is currently being operated in manual mode due to limit switch problems.  All channel/tailwater differentials were in criteria.  Channel/tailwater differential criteria are 1 – 2 feet.

### Auxiliary Water Supply System:  Two of the 3 north shore fish pumps were operated without problems.  The north shore fish pump 1 is out of service due to an electrical problem.  Parts are on order.  Six of 8 south fish pumps are in service.  All south fish pumps are available for operation.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  No problems to report.  Debris is accumulating in the forebay in front of the powerhouse.  Fish ladder exits are clear of debris and the bubblers are operating.  Turbine unit trash rack raking is tentatively scheduled for the week of March 19.

STSs/VBSs:  STSs are raised for annual maintenance and tentatively scheduled to be lowered into operating positions the week of March 19.

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe:   The juvenile fish bypass is not in operation.  All orifices are closed.  The start-up date is tentatively scheduled for March 19.  Repairs to caulking, juvenile collection channel netting, damaged Plexiglas orifice covers, and screen cleaner brush replacement were accomplished during the winter outage.  The primary dewatering screen was inspected along with the supporting structure underneath.  A zebra mussel inspection was performed, none were found.   The concrete in the juvenile collection channel concrete is continuing to deteriorate in places.

Juvenile Bypass Facility:  The bypass is scheduled to be put into operation March 19.

Fish Sampling:  The first sample is scheduled for April 2.  Sampling days will be Monday and Thursday through the beginning of July.

Removable Spillway Weir:  The RSW is currently not in operation.  Spill for fish is expected to begin April 3, 2012.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Ice Harbor Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 41.4 | 32.2 | 0.0 | 0.0 | 40 | 39 | 6.2 | 5.4 |

*Unit 1 scrollcase temperature.

#### Other

Inline Cooling Water Strainers:  Cooling water strainers were inspected on February 16.  Seven live juvenile lampreys were recovered.  Mortalities recovered included 137 juvenile lamprey, 30 peamouths and 1 catfish.

Invasive Species: There were no zebra mussels observed at the monitoring stations on this week.

# Project:  Lower Monumental Dam

# Biologist(s):  William Spurgeon and Elizabeth Lindsey

Dates: March 1 - 8, 2012

## Turbine Operation

All turbine units are being operated within the 1% soft constraint operation criteria.  Unit 4 was removed from service on January 1 for exciter replacement.  Units 5 and 6 were out of service for SQ-2 breaker replacement on March 1 from 1400-1616 hours.  Unit 3 was out of service from 0844 -1615 hours on March 5 for unit 4 exciter interfacing.  Unit 5 was taken out of service for exciter replacement on March 7 at 1605 hours.

Adult Fish Passage Facility

The adult fishway was inspected by Corps biologists on March 1, 5, 6, 7, and 8.

Fish Ladders: Fishway exit head differentials and depths over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively) on all inspections.  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively) on all inspections.  The south shore picketed leads were installed and lowered on February 27.

### Fishway Entrances and Collection Channel: NSE1 and NSE 2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections.  North shore channel/tailwater head was in criteria (1’-2’) on all inspections.

SPE 1 and SPE 2 weir gates were in sill criteria (criteria: > 8’ or on sill) on all inspections.  While on sill, the gate depth readings were 7.5’, 7.2’, 7.5’, 7.4, and 7.4 feet.  SPE 1 was removed from service for re-calibration on March 7 at 1320 hours and returned to service on March 9 at 1605 hours. South powerhouse channel/tailwater head was in criteria (1’-2’) on all inspections.

SSE1 weir gate was in depth criteria (criteria: > 8’ or on sill) on all inspections.  SSE 2 was in criteria (6’ above sill) on all inspections.  South shore channel/tailwater head was in criteria (1’-2’) this week.

### Auxiliary Water Supply System: AWS pumps 1 and 3 were in service and operating throughout this period.  Pump 2 is out of service due to a misaligned diffuser.  Expected date to return to service is 9 April.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 24.4 square yards of forebay debris observed during this period.  Debris will be removed from the gatewells and trash racks during the week of March 19.

STSs/VBSs:  STSs are scheduled to be installed during the week of March 19.  However this date is contingent on the outfall relocation progress.

Orifices, Collection Channel, Dewatering Structure, Flume:   The outfall relocation project is nearing completion.  The bypass is scheduled to be watered up during the week of March 19.  This date is also contingent on the outfall relocation progress.

Collection Facility:  Winter maintenance is being finished up.  The facility is scheduled to be watered up for testing the week of March 19.  This date is also contingent on the outfall relocation progress.

Transport Summary:  No transport.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Monumental Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF)* |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 43.8 | 34.9 | 0 | 0 | 40.0 | 40.5 | 2.8 | 3.7 |

*Scrollcase temperatures.

#### Other

Inline Cooling Water Strainers:  Cooling water strainers were inspected on March 6.  Fifteen live lampreys were recovered.  Mortalities included 99 lampreys.  No other fish species were present.

Invasive Species: There were no zebra mussels observed at the monitoring stations on March 1.

Divers inspected the RSW on February 23.  The RSW is ready for year 2012 spill operations.

Project:  Little Goose

# Biologists: George Melanson

Dates: March 1 - 8, 2012

## Turbine Operation

Turbine units 1 through 6 were available for service throughout most of this report period.  The turbine units were operated within the 1% efficiency soft constraint criteria.

## Adult Fish Passage Facility

The fish ladder and the collection channel were returned to service on February 15.  Both NSE1 and 2 weirs are inoperable and positioned at 531.5 ft.  Both weirs are positioned at best elevation for fish passage for the entire adult fish passage season.

USACE fisheries biologists performed measured inspections of the adult fishway March 1, 5 and 8.

Fish Ladder:  The ladder exit head differentials ranged from 0.0 to 0.1 feet (criteria < 0.5 ft.).  Water depths over the weirs ranged between 1.0 and 1.2 feet (criteria 1.0-1.3 ft.) and picketed lead head differentials was 0.0 (criteria < 0.3 ft.).  No debris was observed at the picketed leads or the ladder exit.  The air bubbler used to prevent debris from collecting near the ladder exit operated satisfactorily.

Fishway Entrances and Collection Channel:  Channel to tailwater head differentials ranged between 1.04 and 1.88 feet (criteria 1.0 to 2.0 ft.).  SSE weir depths ranged between 8.48 and 8.62 feet (criteria ≥8.0 ft), NPE weirs depths ranged between 7.18l and 7.32 feet (criteria ≥7.0 ft or on sill).  NSE weirs remain at fixed elevations of 531.5 feet and depths ranged between 8.14 and 8.54 feet (criteria ≥ 6.0 ft.).  Collection channel surface water velocities (criteria 1.5 fps) ranged from 1.5 to 2.0 fps near the SSE and 2.4 to 2.9 fps near the NSE.

Auxiliary Water Supply System:  All fish pumps operated within criteria this report period.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Woody debris increased this week from none to 300 square feet inside the trash shear boom and up to 1500 square feet outside the trash shear boom.

Spillbay Weir:  The spillbay weir was not in service during this report period.

ESBS/VBS:  All ESBSs remained raised and in their winter storage positions.  Maintenance is ongoing.

Orifices, Collection Channel, Dewatering Structure, Flume:  The juvenile collection system is out of service for winter maintenance.

Transportation Facility:  The facility is out of service for winter maintenance.

Transport Summary:  Transport operations are expected to begin in late April or early May.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Little Goose Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 39.2 | 34.0 | 0 | 0 | 40.0 | 39.6 | 6.0 | 1.8 |

*Ladder temperature.

Other

Inline Cooling Water Strainers:  On March 8, cooling water strainers were inspected.  A total of 223 juvenile lamprey mortalities were removed.  A total of 55 live juvenile lamprey were recovered and released in the tailrace in fair to poor condition.  The next inspection is scheduled for March 15.

Invasive Species:  The zebra mussel substrate monitor is scheduled for inspection on April 5.

Avian Activity: Seagull numbers increased this week with up to 30 observed on Monday, March 5 and actively feeding on juvenile lamprey. By Thursday, March 8 only the occasional gull was      observed.

Project:  Lower Granite

# Biologist(s):  Mike Halter and Ches Brooks

Dates: March 1 - 8, 2012

## Turbine Operation

Lower Granite had turbine units 2, 4 and 5 available for power generation at the beginning of the report period.  Turbine unit 1 is out of service at the present time and is undergoing testing.  The turbine blades have been welded at a fixed angle to address the malfunction of the blade linkages that were found during annual maintenance.  The tentative return to service date for this unit is mid March. Turbine unit 3 is out of service for cavitation repair.  The tentative return to service date for this unit is March 28.  Turbine unit 6 was taken out of service on February 21 in order to address brake and governor issues.  Turbine unit 6 was returned to service at 0947 hours on March 2.

## Adult Fish Passage Facility

On March 1, 5, 6 and 7, Lower Granite fisheries biologists performed measured inspections of the adult fishway system.

Fish Ladder:  All criteria were met.

Fishway Entrances and Collection Channel:  Head differential readings remained within criteria at the south shore and north powerhouse adult fishway entrances during the period inspections.  The north shore entrances were in criteria on the March 1 inspection but failed to meet criteria (criterion 1.0 – 2.0 feet) on the subsequent inspections with head differentials of 0.5, 0.7 and 0.8 feet respectively.  Only north shore entrance 2 can adjust depth relative to the tailwater elevation (see below) making it difficult to achieve the requisite head differential.  Weir depths at the south shore fishway entrances met criteria during the period inspections.  Weir gates at the north powerhouse entrances were on sill during the March 6 inspection due to low tailwater elevations (these weirs bottom out at 636.0 feet) both gates had an elevation of 7.3 feet.  On the other inspections higher tailrace levels allowed these gates to meet depth criteria (criterion ≥ 8.0 feet).  Weir depths at the north shore entrances ranged from 3.3 to 9.7 feet (criterion ≥ 7.0 feet).  North shore entrance 1 has been manually dogged off at 628.5 feet which is creating more weir depth than necessary at the loss of head differential.  This condition has been reported to the operators.  Normally weir depth readings at the north shore entrances are sacrificed in order to maintain the requisite 1.0 foot of head differential.  Velocity readings in the adult fishway collection channel transition pool area ranged from 0.91 to 1.04 feet per second and averaged 0.98 feet per second.

### Auxiliary Water Supply System:  Fish pumps 2 and 3 were operated during the week.  Fish pump 1 is out of service because Babbitt (a bearing surface metal) was detected in the oil, indicating a potential bearing problem.

#### Juvenile Fish Passage Facility

The juvenile collection/bypass system has been shut down for the winter outage since December 19, 2011.  Water up of the collection gallery and initiation of primary bypass at the separator is tentatively scheduled for March 21.  Sampling activities are scheduled to begin on March 25.

Forebay Debris/Gatewell Debris/Oil:  Forebay debris removal and trash rack raking was completed by February 27.

ESBSs/VBSs:  The ESBSs were dogged-off for maintenance work during the week.  Deployment of ESBSs is tentatively scheduled to begin during the third week of March.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  Inspection by submersible camera revealed some cable and metal material stuck in the separator upwell area, fish facility personnel were able to remove this debris using a grappling hook and pike pole.  Further inspection by camera confirmed that this area is clear of debris.

Transportation Facility:  General barge transport operations are up in the air at this time but will probably begin in early May.  Research barging operations will probably begin sometime in April.  Juvenile fish sampling (only) activities are tentatively scheduled to begin on March 25.

Transport Summary:  Nothing to report.

Removable Spillway Weir:   Nothing to report on the RSW.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Granite Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 39.3 | 35.2 | 0.0 | 0.0 | 43.0 | 42.3 | 4.6 | 2.4 |

*Scrollcase temperature.

Other

Inline Cooling Water Strainers:  The most recent cooling water strainer inspections took place on February 28.  A total of 496 juvenile lamprey mortalities were recovered from turbine units 2, 4, 5 and 6.  Turbine units 1 and 3 are undergoing extensive maintenance and are under clearance.

Invasive Species:  The mussel trap was inspected this week and no invasive species were found.

Video counts in the adult fish ladder counting room began on March 1.  The recording hours are from 0600 to 1600 hours.

The adult fish trap was watered up and sampling began on March 8.  The initial sample rate will be set at 10%.  Scale samples will be taken from one out of every 20 hatchery steelhead.  All wild steelhead captured will be PIT-tagged and scale and genetic samples taken.  Any previously PIT-tagged steelhead (either hatchery or wild) will have both scale and genetic samples taken for verification purposes.