U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

#### FISH FACILITIES WEEKLY REPORT

#02-2012

# Project:  McNary

# Biologists: Carl Dugger and Bobby Johnson

Dates: March 9 - 15, 2012

## Turbine Operation

McNary had eight to 13 turbine units available for power generation this week.  Unit outages are recorded in Table 1.  The operating project does not know when unit 1 will return to service.

Table 1.  Turbine Unit Outages at McNary Dam.

| Units | Outage Dates | Outage Length | Reason |
| --- | --- | --- | --- |
| 1 | All week. | All week. | Oil leak after rewind. |
| 12, 13, 14 | Mar 10. | 8.3 hours total. | Dive contract. |
| 5 | Mar 12 to Apr 26. | Approx. 45 days. | Relay upgrade. |
| 6 | Mar 12 to Apr 19. | Approx. 38 days. | Relay upgrade. |
| 14 | Mar 14 to 16. | 55 hours. | Transmission line restriction. |
| 7,8 | Mar 15 to 19. | Approx. 4 days. | Relay upgrade. |

On April 1, the hard constraint one percent criteria will begin.

## Adult Fish Passage Facilities

On March 11, 14, and 15, the McNary fisheries biologist performed measured inspections of the adult fishways.  Video adult fish counting continues.

### Fish Ladders:  Both ladders me all Fish Passage Plan criteria during measured inspections.

### At the Oregon exit, project personnel adjusted the set points once.  The south traveling screen had repeated false alarms, which the operators reset.  Screen differential monitoring revealed no problems.

Fishway Entrances and Collection Channel:  All Washington ladder inspection points were in criteria, except on March 14 and 15 when weir W3 measured depths of 7.8 and 7.9 feet, respectively, due to low tailwater.  The technical staff reported that the weir reached its bottom limit.

Most Oregon ladder inspection points met criteria.  Discrepancies included the north powerhouse pool differential (measured from 0.7 to 0.8 feet) and the north entrance weirs, NFEW2 and NFEW3 (depths measured 8.6 to 8.9 feet).  These readings were due to the juvenile facility being out of service and low tailwater elevations at times.  On March 14, the south pool differential measured 0.9 feet.  This may be due to the weirs running deep that day.  All other Oregon inspection points were in criteria.  Collection channel velocities averaged 1.4 feet per second.  The project will install a new velocity meter in the near future.

### Auxiliary Water Supply System:  For the week, fish pumps 1 and 3 were operated with blade angles of 30 degrees and one interruption in service on March 12 due to a power outage.  The length of the outage was not recorded but it was brief.  Pump 2 remains out of service for major overhaul which will require a contract.

### The juvenile fish facility is not yet supplying the usual 450 cfs to the north powerhouse pool.

### The Wasco County PUD had no interruptions in service.  The project is working with the PUD to refasten the two loose bypass diffusers in the near future.

#### Juvenile Fish Passage Facility

The facility remains shut down for winter maintenance, which is nearing completion.  By March 21, the contractor will have completed most work on the new primary and secondary bypass lines along with the PIT and adult return lines.  On March 22, the project will test the system.

Forebay Debris/Gatewell Debris/Oil:  For the week, forebay debris was light but increasing due to incoming woody debris and tumbleweeds.   During the week, the fisheries staff monitored trash rack differentials.  No problems were seen.  The project should complete work on the intake deck crane trash hoist next week, at which time trash rack cleaning can resume.

This week, a slight amount of fish screen oil was observed in one slot and subsequently removed with absorbent pads.

ESBSs/VBSs:  All ESBSs remain raised and the project has almost concluded maintenance.  The project plans to install the screens from April 5 to 15 in a manner similar to the last three seasons in support of juvenile lamprey passage.

VBS differential monitoring will resume when ESBS installations begins.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  The orifices remain closed for winter maintenance, which is nearly concluded.  The electrical staff replaced three orifice attraction lights and three light switches.  The fisheries staff installed two steps over orifices at the traps and cleaned the channel along with the orifice covers.

The channel will be re-watered and bypass operations will begin in late March.

Transportation Facility:  The facility remains dewatered for winter maintenance which is nearing completion.  The fisheries staff replaced the primary gate gaskets and repaired the seal on the new raceway tailscreens.

Transport Summary:  Fish transport in not in progress at this time.

River Conditions

River conditions during the week are outlined in Table 2 as provided by control room.  Data days run from 0000 to 2400 hours.  The project plans to install the rehabilitated TSWs before April 10.  Water temperature is taken from the unit 1 scroll case.  Spill began March 14, due to river flow in excess of power house capacity.

Table 2.  River conditions at McNary Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 164.3 | 123.9 | 61.6 | 0.0 | 40 | 40 | 6.0 | 6.0 |

Other

Inline Cooling Water Strainers:  On March 20 the facility personnel will examine the main unit cooling water strainers.

Invasive Species:  The biologist will examine the zebra mussel stations later this month.

Predatory Bird Observations:  Bird counts will resume later in the month when technicians are on shifts.  This week, in the tailwater area, biologists observed an occasional gull or cormorant.  On the first day of spill, ten gulls were observed.  The bypass system is not functional, so there are no birds to observe at the outfall.  At times five grebes were observed in the forebay area.

Research:  The adult fallback study continues.  Other researchers are preparing for juvenile salmonid and adult lamprey passage studies.

Project:  Ice Harbor

# Biologist:  Mark Plummer

Biological Technician:  Stephen Jeffers

Dates: March 9 - 15, 2012

## Turbine Operation

Turbine units 1- 4 and 6 were available for operation this reporting period.  Turbine unit 2 returned to service March 10 at 1504 hours.  Turbine unit 3 returned to service March 14 at 1415 hours.  Turbine unit 5 remained out of service this period.   Turbine units 3 and 5 trash racks were raked for debris March 14.  No debris was found in either turbine unit.

## Adult Fish Passage Facilities

### Fish facility personnel inspected the adult fishways March 12, 13, and 15.

### Fish Ladders:  All north and south adult fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria.

### Fishway Entrances and Collection Channel (inspection date order):  The south shore entrance (SFE) was off sill with a depth of 8.1 feet, off sill with a depth of 8.4 feet, and off sill with a depth of 8.2 feet.  The north powerhouse entrance (NFE) was off sill with a depth of 9.4 feet, off sill with a depth of 10.8 feet, and off sill with a depth of 9.3 feet.  The north shore entrance (NSE) was off sill with a depth of 9.3 feet, off sill with a depth of 9.4 feet, and off sill with a depth of 8.5 feet.  Fishway entrance criterion is 8 feet depth, greater than 8 feet depth, or on sill.  The NFE is currently being operated in manual mode due to limit switch problems.  The parts to fix the problem are being identified and researched.  All channel/tailwater differentials were in criteria.  Channel/tailwater differential criteria are 1 – 2 feet.  Channel velocities ranged from 1.7 – 2.3 fps.

### Auxiliary Water Supply System:  Two of the 3 north shore fish pumps were operated without problems.  The north shore fish pump 1 is out of service due to an electrical problem.  Parts are currently on order.  Six of 8 south fish pumps are in service.  All south fish pumps are available for operation.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  No problems to report.  Debris is accumulating in the forebay in front of the powerhouse.  Fish ladder exits are clear of debris and the bubblers are operating satisfactorily.  Turbine unit trash rack raking is tentatively scheduled for the week of March 19.

STSs/VBSs:  STSs are raised for annual maintenance and are tentatively scheduled to be lowered into operating position the week of March 19.

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe:   The juvenile fish bypass is not in operation.  All orifices are closed.  Startup date is tentatively scheduled for March 19.

Juvenile Bypass Facility:  The bypass is scheduled to be placed into operation March 19.

Fish Sampling:  The first sample is scheduled for April 2.  Sampling days will be Monday and Thursday through the beginning of July.

Removable Spillway Weir:  The RSW is currently not in operation.  Spill for fish is expected to begin April 3, 2012.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Ice Harbor Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 58.9 | 35.5 | 0.0 | 0.0 | 41 | 40 | 5.6 | 4.5 |

*Unit 1 scrollcase temperature.

Other

Inline Cooling Water Strainers: Turbine unit 3 cooling water strainer was cleaned March 14.  1 live juvenile lamprey was found along with 9 dead juvenile lampreys.

Invasive Species: No zebra mussels were observed during fishway inspections.

# Project:  Lower Monumental Dam

# Biologist(s):  William Spurgeon and Elizabeth Lindsey

Dates: March 9 - 15, 2012

## Turbine Operation

All available turbine units are being operated in soft constraint of the 1% operation criteria.  Unit 4 was removed from service on January 1 for exciter replacement.  Unit 5 was taken out of service for exciter replacement on March 7 at 1605 hours.  Unit 3 was out of service from 1155 -1521 hours on March 9 in support of unit 4 exciter interfacing.

Adult Fish Passage Facility

The adult fishway was inspected by Corps biologists on March 12, 13, 14, and 15.

Fish Ladders: Fishway exit head differentials and depths over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively) on all inspections.  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively) on all inspections.  The south shore picketed leads were installed on February 27.

### Fishway Entrances and Collection Channel: NSE1 and NSE 2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections.  North shore channel/tailwater head was in criteria (1’-2’) on all inspections.

SPE 1 and SPE 2 weir gates were in sill criteria (criteria: > 8’ or on sill) on all inspections.  While on sill, the gate depth readings were 7.5 feet.  SPE 1 was removed from service for re-calibration on March 7 at 1320 hours and returned to service on March 9 at 1605 hours. South powerhouse channel/tailwater head was in criteria (1’-2’) on all inspections.

SSE1 weir gate was in depth criteria (criteria: > 8’ or on sill) on all inspections.  SSE 2 was in criteria (6’ above sill) on all inspections.  South shore channel/tailwater head was in criteria (1’-2’) this week.

### Auxiliary Water Supply System: AWS pumps 1 and 3 were in service and operating throughout this period.  Pump 2 is out of service due to a misaligned diffuser.  Expected date to return to service is 9 April.  All pumps were out of service on for emergency diesel generator installation from 1711- 1930 hours on March 15.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 37.5 square yards of forebay debris observed during this period.  Debris will be removed from the gatewells and trash racks during the week of March 19.

STSs/VBSs:  The STSs were inspected via rotation on deck on March 14.  All screens were ready for deployment. STSs are scheduled to be installed during the week of March 19.  This date is contingent on the outfall relocation progress as it requires watering up of the bypass outfall.

Orifices, Collection Channel, Dewatering Structure, Flume:   The outfall relocation project is nearing completion.  The bypass is scheduled to be watered up during the week of March 19; this date is also contingent on the outfall relocation progress.

Collection Facility:  Winter maintenance is being finished up.  The facility is scheduled to be watered up for testing the week of March 19.

Transport Summary:  Transport operations are not taking place at this time.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Monumental Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF)* |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 58.6 | 36.8 | 0 | 0 | 41.5 | 41.0 | 4.0 | 2.7 |

*Scrollcase temperatures.

#### Other

Inline Cooling Water Strainers:  Cooling water strainers were inspected on March 6.  Fifteen live lampreys were recovered.  Mortalities included 99 lampreys.  No other fish species were present.

Invasive Species:  There were no zebra mussels observed at the monitoring stations on March 1.

Project:  Little Goose

# Biologists: George Melanson

Dates: March 9 - 15, 2012

## Turbine Operation

Turbine units 1 through 6 were available for service throughout this report period.  All turbine units were operated within the 1% efficiency soft constraint criteria.

## Adult Fish Passage Facility

USACE fisheries biologists performed measured inspections of the adult fishway March 12, 14 and 15.

Fish Ladder: The ladder exit head differentials ranged from 0.0 to 0.1 feet (criteria < 0.5 ft.).  Water depths over the weirs held steady at 1.1 feet (criteria 1.0-1.3 ft.) and picketed lead head differentials measured 0.0 (criteria < 0.3 ft.) on all inspections.  No debris was observed at the picketed leads or the ladder exit.  The air bubbler used to prevent debris from collecting near the ladder exit operated satisfactorily.

Fishway Entrances and Collection Channel:  Channel to tailwater head differentials ranged between 1.06 and 1.70 feet (criteria 1.0 to 2.0 ft.).  SSE weir depths ranged between 8.42 and 8.54 feet (criteria ≥8.0 ft), NPE weirs depths ranged between 6.70 and 7.30 feet (criteria ≥7.0 ft or on sill).  NSE weirs remain at fixed elevations of 531.5 feet and depths ranged between 7.4 and 8.54 feet (criteria ≥ 6.0 ft.).  Collection channel surface water velocities (criteria 1.5 fps) ranged from 1.8 to 1.9 fps near the SSE and 2.4 to 2.5 fps near the NSE.

Auxiliary Water Supply System:  All fish pumps operated within criteria this report period.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Up to 300 square feet of woody debris was observed inside the trash shear boom.    Turbine unit trash racks were raked on March 13 and 15.  Approximately 80 yards of woody debris was removed.  The majority of debris was removed from racks associated with units 1 and 2.  Trash rack raking is scheduled to continue on units 1 and 2.

Spillway Weir:  The spillway weir was not in service during this report period.

ESBS/VBS:  All ESBS remained raised and in their winter storage positions.  Maintenance is ongoing.  ESBS deployment is scheduled to begin March 19.

Orifices, Collection Channel, Dewatering Structure, Flume:  The juvenile collection system is out of service for winter maintenance.

Transportation Facility:  The facility is out of service for winter maintenance.

Transport Summary:  Transport operations are expected to begin in late April or early May.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Little Goose Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 54.1 | 33.6 | 0 | 0 | 41.5 | 40.4 | 5.4 | 4.2 |

*Ladder temperature.

Other

Inline Cooling Water Strainers:  On March 15, cooling water strainers were inspected.  A total of 85 dead juvenile lamprey were removed.  The next inspection is scheduled for March 22.

Invasive Species:  The Zebra Mussel substrate monitor is scheduled for inspection on April 5.

Avian Activity: The occasional seagull was observed this week.

Project:  Lower Granite

# Biologist(s):  Mike Halter and Ches Brooks

Dates: March 9 - 15, 2012

## Turbine Operation

Lower Granite had turbine units 2, 4, 5 and 6 available for power generation at the beginning of the report period.  Turbine unit 1 was returned to service at 0630 hours on March 13.  The turbine blades for unit 1 have been welded at a fixed angle.  Turbine unit 2 was forced out of service on March 13 at 0645 hours because of a regulator problem detected at start up; this unit was returned to service at 0751 hours on March 14.  Turbine unit 3 is out of service for cavitation repair.  The tentative return to service date for this unit is March 28.

## Adult Fish Passage Facility

On March 12, 13, and 14 the Lower Granite fisheries biologists performed measured inspections of the adult fishway system.

Fish Ladder:  All criteria were met.

Fishway Entrances and Collection Channel:  Head differential readings remained within criteria at the south shore and north powerhouse adult fishway entrances during the weekly inspections.  The north shore entrances were out of criteria on all inspections (criterion 1.0 – 2.0 feet).  The head differentials for the north shore entrances were 0.6, 0.5 and 0.7 feet respectively.  Only north shore entrance 2 can adjust depth relative to the tailwater elevation (see below) making it difficult to achieve the requisite head differential.  Weir depths at the south shore fishway entrances met criteria during the weekly inspections.  Weir gates at the north powerhouse entrances were on sill during the March 14 inspection due to low tailwater elevations (these weirs bottom out at 636.0 feet) both gates had an elevation of 7.0 feet.  On the other inspections higher tailrace levels allowed these gates to meet depth criteria (criterion ≥ 8.0 feet).  Weir depths at the north shore entrances ranged from 3.8 to 8.6 feet (criterion ≥ 7.0 feet).  North shore entrance 1 has been manually dogged off at 628.5 feet which is creating more weir depth than necessary, reducing head differential.  This condition has been reported to the operators.  Normally weir depth readings at the north shore entrances are sacrificed in order to maintain the requisite 1.0 foot of head differential.  Velocity readings in the adult fishway collection channel transition pool area ranged from 0.86 to 1.06 feet per second and averaged 0.98 feet per second.

### Auxiliary Water Supply System:  Fish pumps 2 and 3 were operated during the week.  Fish pump 1 is out of service because Babbitt (a bearing surface metal) was detected in the oil, indicating a potential bearing problem.

#### Juvenile Fish Passage Facility

The juvenile collection/bypass system has been shut down for the winter outage since December 19, 2011.  Water up of the collection gallery and initiation of primary bypass at the separator is tentatively scheduled for March 21.  Sampling activities are scheduled to begin on March 25.

Forebay Debris/Gatewell Debris/Oil:  Forebay debris removal and trash rack raking was completed by February 27.

ESBSs/VBSs:  The ESBSs were dogged-off for maintenance work during the week.  Deployment of ESBSs is tentatively scheduled to begin during the third week of March.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  Nothing to report at this time.

Transportation Facility:  A new controller valve (which controls the inclined screen/primary dewatering system on the separator) was installed on the morning of March 14.  General barge transport operations are uncertain at this time but will probably begin in early May.  Research barging operations will probably begin sometime in April.  Juvenile fish sampling (only) activities are scheduled to begin on March 25.

Transport Summary:  Fish transport operations are not in progress at this time.

Removable Spillway Weir:   The RSW is ready for service.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Granite Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 52.4 | 33.8 | 0.0 | 0.0 | 44.9 | 43.7 | 4.4 | 3.8 |

*Scrollcase temperature.

Other

Inline Cooling Water Strainers:  Cooling water strainers were inspected for lamprey entrainment on February 28.  A total of 496 lamprey were found in the strainers over a combined run time of 1454 unit hours.  Units 1 and 3 were out of service and were not inspected.

Invasive Species:  The zebra mussel trap at the adult fishway exit was replaced with a new trap using scrub pad material on March 12.

Video counts in the adult fish ladder counting room began on March 1.  The recording hours are from 0600 to 1600 hours.

Adult fish trap operations continued with a sample rate of 10%.  Scale samples will be taken from one out of every 20 hatchery steelhead.  All wild steelhead captured will be PIT-tagged and have scale and genetic samples taken.  Any previously PIT-tagged steelhead (either hatchery or wild) will have both scale and genetic samples taken for verification purposes.