U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

#### FISH FACILITIES WEEKLY REPORT

#09-2012

# Project:  McNary

# Biologists: Carl Dugger and Bobby Johnson

Dates: April 27 – May 3, 2012

## Turbine Operation

McNary had 12 units available for power generation this week.  Unit outages are recorded in Table 1.

Table 1.  Unit Outages at McNary Dam.

| Units | Outage Dates | Outage Length | Reason |
| --- | --- | --- | --- |
| 5 and 6 | To Apr 27. | 46 days. | Relay upgrade. |
| 7 and 8 | Apr 27. | 4.0 hours. | Units 5 and 6, testing. |
| 10 | Apr 30. | 4.1 hours. | ESBS replaced, C slot. |

On April 1, the hard constraint one percent criteria began.  No units ran outside the criteria.

## Adult Fish Passage Facilities

On April 27, 29 and May 1, the McNary fisheries biologist performed measured inspections of the adult fishways.  Visual fish counting continues.

### Fish Ladders:  During measured inspections, all Fish Passage Plan criteria were met on both ladders.

### At the Washington exit, debris has increased in the area with the project cleaning the leads almost daily including general maintenance coming in on the weekend.

### At the Oregon exit, the south traveling screen had multiple alarms which the operators reset.  Also, the traveling screens’ wash pump alarmed once and was reset.  Screen differential monitoring revealed no problems.  On April 27, the biologist found the traveling screens’ debris trough and discharge pipe obstructed with debris.  The biologist was able to clean the trough.  However, the project is investigating how to clear the discharge pipe’s partial blockage.

Fishway Entrances and Collection Channel:  Spill turbulence and hydraulic gradients make it difficult for the project to maintain entrance weir depth and calibration.

On the Washington ladder, the biologist found all inspection points in criteria.

All week, the south powerhouse entrances, SFEW1 and SFEW2, measured 8.7 to 8.9 and 7.2 to 8.3 feet, respectively.  These readings are due to hydraulic gradients.  It is also possible the stilts on SFEW2 are affecting the flow out of the south entrances.  The project was able to maintain the south pool differential at 1.0 to 1.1 feet.  All other Oregon inspection points were in criteria.

The collection channel velocity average 1.4 feet per second.  On May 3, the project attempted to install a new velocity meter probe.  However, we discovered we could not install the probe in the still well currently being used because we could not remove the old probe.  It appears the new probe can not be installed until the ladder is dewatered for winter maintenance.

### Auxiliary Water Supply System:  For the week, fish pumps 1 and 3 were in service with blade angles of 30 degrees with one interruption.  On April 29, from 1920 to 1932, pump 1 was out of service due to a grease pump failure.  Pump 2 remains out of service for major overhaul which will require a contract.

### The juvenile facility continues to provide the usual 450 cfs to the north powerhouse pool.

### The Wasco County PUD had no interruptions.

#### Juvenile Fish Passage Facility

The spring bypass season continues with alternating days of primary and secondary bypass with the switch occurring every morning at 0700 hours.  No deviation from this schedule occurred.  This data week, 437,409 smolts and 32,500 juvenile lampreys were bypassed.

Forebay Debris/Gatewell Debris/Oil:  For the week, forebay debris was very light to light with location affect by project operations, flow and wind patterns.  Much of the residue and incoming debris passed over the TSW’s.  The fisheries staff monitored trash rack differentials with no problems seen.  The project will clean trash racks in mid May.

This week, the fisheries staff observed no problems in the gatewell slots.

ESBSs/VBSs:  The project has ESBS’s installed at all units.  On April 30, though functional, the project replaced the screen in 10C slot due to an electrical problem.  From April 28 to May 2, the screen in 7C slot was in bypass mode due to a cycling issue which the operators resolved.  On May 8, the fisheries staff will begin ESBS camera inspections.

The fisheries staff monitored VBS differential with no problems found.  On May 3, the maintenance crew drilled a hole in the VBS slot cover at 4A slot improving the accuracy of differential measurements.  In June, the project will resume VBS rehabilitation.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe: This week, 42 orifices were in use with no blockages observed.  The fisheries mechanic continues to refurbish the orifice controllers and has parts on order.

All systems operated well in automatic mode.  The transition screen cleaning device remains out of service until a channel shutdown occurs.  The fisheries staff monitored the channel on all shifts when in primary bypass.

Transportation Facility:  With the spring bypass season, both bypass modes return all fish are to the river.  PIT tag detection will occur in the full flow pipe during primary bypass and throughout the facility during secondary bypass.  Smolt monitoring will occur on secondary bypass days.

The primary (A and B) PIT tag slide gates remain off and closed as the return to river lines provide a better bypass route for PIT tagged fish.  Starting May 8, NMFS will use this system as part of a steelhead straying study.  The secondary (C and D) PIT/bypass gates were off and open.  The fisheries staff turns the sample gates off or on at 0700 hours each day so the gates will be functional during secondary bypass.

Ice block checks of the return to river lines revealed no blockages.  However, due to the new location of the bypass outfall and high tailwater elevations, the fisheries staff is having difficulty seeing the ice blocks exit the pipe.  A spotting scope is on order.

This week, the fisheries staff repaired the A side sample tank net.

On April 1 and 3, after releasing the sample raceway, the biologist noted a total of six unclipped sockeye smolts under the new barge/bypass gate.  Five of these were lost.  On April 3, the contractor and fisheries mechanics lowered the gate and clamped it in place.  Next week, the contractor will complete adjustments to the gate.

Transport Summary:  There is nothing to report.

River Conditions

River conditions during the week are outlined in Table 2 which the smolt monitoring staff provides.  The data day is from 0700 to 0700 hours.  The spring spill program calls for 40 percent of flow being spilled.  Due to high flows, 54 to 61 percent was spilled.

Table 2.  River conditions at McNary Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF) |  | Water Clarity* (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 409.8 | 371.8 | 274.5 | 207.0 | 50.8 | 49.2 | 3.1 | 2.7 |

*Control room data.

Other

Inline Cooling Water Strainers:  The project will do the next project main unit cooling water strainer examination in mid May.

Invasive Species:  The next zebra mussel stations’ examination will occur in late May.

Predatory Bird Observations:  APHIS continues hazing and day shift technicians do the bird counts.  In the tailwater area, we saw a high count of 200 gulls with an occasional pelican, loon, or tern.  The birds were mostly in the area of the spill feeding or roosting.

We noted a high count of 167 gulls by the bypass outfall.  Generally, about 30 gulls were noted there.  The water cannon remains out of service until flows decrease to a level that accessing the pump will not be a safety issue.  Also, the project needs to develop an access protocol which will begin next week.

In the forebay area, we observed a high count of 40 grebes and ten gulls with an occasional pelican, osprey and loon noted.  Hazing appears to be working well on grebes.  Occasionally, a raft of pelicans or gulls was noted in the forebay upstream of the spill.  Also, the biologist observed pelicans on the roosting rocks by the Washington shore boat dock.

The one grebe in the gatewell slots passed through the system to the separator where a technician released it.

Research:  The juvenile salmonid and steelhead kelt passage studies continue.  The contractor has delayed the Oregon exit traveling screen study.  Researchers are preparing for the adult lamprey passage study.  GBT monitoring continues.

Project:  Ice Harbor

# Biologist:  Mark Plummer

Biological Technician:  Stephen Jeffers

Dates: April 27 – May 3, 2012

## Turbine Operation

Turbine units 1 – 4 and 6 were available for operation this reporting period.  Turbine unit 5 remained out of service.

## Adult Fish Passage Facilities

### Fish facility personnel inspected the adult fishways April 30, May 1, May 2, and May 3.

### Fish Ladders:  All north and south adult fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria, except on the May 3 inspection. On this inspection, the north channel/tailwater differential was 2.1 feet.  Channel/tailwater differential criterion is 1 – 2 feet.

### Fishway Entrances and Collection Channel (inspection date order):  The south shore entrance (SFE) was off sill with a depth of 6.7 feet, off sill with a depth of 8.5 feet, off sill with a depth of 7.6 feet, and off sill with a depth of 7.1 feet.  The north powerhouse entrance (NFE) was off sill with a depth of 13.2 feet, off sill with a depth of 13.9 feet, off sill with 13.7 feet, and off sill with a depth of 13.1 feet.  Spill is causing the NFE to become stuck in the entrance guides and it cannot be raised or lowered.  This condition will also affect the south shore adult fish entrance depths due to a common water channel shared with the NFE.  The north shore entrance (NSE) was off sill with a depth of 8.5 feet, off sill with a depth of 9.5 feet, off sill with 8.9 feet, and off sill with a depth of 8.6 feet.  All out of criteria events at the NSE were reported to the control room operator to adjust the entrance depth.  The NSE is currently being operated in manual mode due to spill.  The NSE water elevation radar sensing unit at tailwater has been put in standby and the control/level indication switched to the metra-tape stilling well system due to tailwater elevation fluctuations caused by spill producing erroneous indications.  Fishway entrance criterion is 8 feet depth, greater than 8 feet depth, or on sill.  Channel velocities ranged from 1.4 fps – 2.3 fps.  Channel velocity criterion is 1.5 fps – 4.0 fps.

### Auxiliary Water Supply System:  2 of the 3 north shore fish pumps were operated without problems.  North shore fish pump 1 is out of service due to an electrical problem.  Parts are on order.  South fish pump 1 was started May 2 at 0200 hours.  7 of 8 south fish pumps are operating.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  No problems to report.  Fish ladder exits are clear of debris and the bubblers are operating.

STSs/VBSs:  The STS are in cycle run timing mode.  April STS and Turbine cooling water strainer inspections were schedule for April 24 and 25.  STS inspections were cancelled due to high flow and river gassing at Ice Harbor.   May inspections are scheduled for May 22 and 23.

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe:  The juvenile fish bypass was put in operation March 19.  20 orifices are open.

Juvenile Bypass Facility:  The bypass was put into operation March 19.

Fish Sampling:

April 30:

| Species | Sampled | #Descaled | Morts | Avian Marks |
| --- | --- | --- | --- | --- |
| C-CH | 49 | 1 | 0 | 1 |
| UC-CH | 27 | 1 | 0 | 0 |
| C-CH-O | --- | --- | --- | --- |
| UC-CH-O | --- | --- | --- | --- |
| C-SH | 54 | 7 | 0 | 2 |
| UC-SH | 20 | 1 | 0 | 2 |
| C-COHO | --- | --- | --- | --- |
| UC-COHO | --- | --- | --- | --- |
| C-SOCK | --- | --- | --- | --- |
| UC-SOCK | --- | --- | --- | --- |
| TOTAL | 150 | 10 | 0 | 5 |

May 3:

| Species | Sampled | #Descaled | Morts | Avian Marks |
| --- | --- | --- | --- | --- |
| C-CH | 84 | 1 | 0 | 1 |
| UC-CH | 33 | 0 | 0 | 0 |
| C-CH-O | --- | --- | --- | --- |
| UC-CH-O | 1 | 0 | 0 | 0 |
| C-SH | 34 | 1 | 0 | 4 |
| UC-SH | 17 | 0 | 0 | 0 |
| C-COHO | 1 | 0 | 0 | 0 |
| UC-COHO | 1 | 0 | 0 | 0 |
| C-SOCK | --- | --- | --- | --- |
| UC-SOCK | --- | --- | --- | --- |
| TOTAL | 171 | 2 | 0 | 5 |

Removable Spillway Weir:  The RSW is in operation.  Spill for fish began April 3, 2012.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Ice Harbor Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 192.2 | 123.4 | 123.5 | 71.5 | 52 | 51 | 3.8 | 1.8 |

*Unit 1 scrollcase temperature.

Other

Inline Cooling Water Strainers: Main turbine cooling water strainer inspections were last inspected April 24 and 26.  Fish recovered included 27 lamprey, 1 juvenile steelhead and 1 catfish.

Invasive Species: No zebra mussels were observed during fishway inspections.

# Project:  Lower Monumental Dam

# Biologist(s):  William Spurgeon and Elizabeth Lindsey

Dates: April 27 – May 3, 2012

## Turbine Operation

The units are being operated in hard constraint of the 1% operation criteria.  Unit 2 was out of service from April 26 at 0705 hours to April 27 at 1746 hours for wicket gate servo packing.   Units 1 through 5 were rotated out of service for STS inspections on May 1, 2 and 3.  Unit 2 was taken out of service at 1025 hours on May 1 due to a damaged STS screen in gatewell slot 2C.  The unit was returned to service at 1107 hours on May 2.  Unit 4 was taken out of service at 1121 hours on May 2 due to damaged STS screens in gatewell slots 4B and 4C.  The unit was returned to service at 1615 hours on May 3.  Unit 5 was taken out of service at 0701 hours on May 3 due to a damaged STS screen in gatewell slot 5A.  Unit was returned to service at 1755 hours on May 3.  Unit 5 tripped and is out of service due to high current and voltage indications that occurred at 2100 hours on May 3.  The problem is being investigated.

Adult Fish Passage Facility

The adult fishway was inspected by Corps and State biologists on April 28, 29, 30, and May 2.

Fish Ladders: Fishway exit head differentials and depths over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively) on all inspections.  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively) on all inspections.

### Fishway Entrances and Collection Channel: NSE1 and NSE 2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections.  North shore channel/tailwater head was in criteria (1’-2’) on all inspections.  SPE 1 and SPE 2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections.  South powerhouse channel/tailwater head was in criteria (1’-2’) on all inspections.  SSE1 weir gate was in depth criteria (criteria: > 8’ or on sill) on all inspections.  SSE 2 was in criteria (6’ above sill) on all inspections.  South shore channel/tailwater head was in criteria (1’-2’) this week.  The collection channel velocity remained in criteria (1.5-4.0 ft/sec) this week.

### Auxiliary Water Supply System:  All AWS pumps were in service and operating through this period.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 74.5 square yards of forebay debris observed during this period.  Gatewell debris ranged from 0-45% surface coverage.

STSs/VBSs:  STSs are operating in cycle mode.  STS’s 1, 2, 3, 4 and 5 were inspected on May 1, 2, and 3.  STS’s from slot 2C, 4B, 4C and 5A required repair due to failure of mesh retainer clips.  STS’s were returned to service on May 2 (2C) and on May 3 (4B, 4C and 5A).  During winter maintenance a new softer plastic clip was used to secure STS mesh.   It has been determined that these clips are unable to withstand the stresses at the overlapping seams of two screen panels.  All new style clips on screen panel overlaps of all screens will be replaced next week.  Additionally, woody debris may have been a factor in at least one slot (2C).

Orifices, Collection Channel, Dewatering Structure, Flume:  The collection channel is operating with 21 orifices open.

Collection Facility:  Daily fish collection for research began on April 25.  Fish were collected at a 100% sample rate until the target number of fish was obtained.  At that time the system was returned to primary bypass.  On May 1 and 2 the facility was operated in secondary bypass when not sampling to allow for training facility operating personnel.  Twenty-four hour sampling was initiated at 1500 hours on May 3 in secondary bypass operation.  Collection for transport is scheduled to begin on May 5 at 0700 hours.

Transport Summary:  No transport.  Every-day barging is scheduled to begin on May 6.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Monumental Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF)* |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 192.6 | 129.3 | 90.4 | 36.6 | 53.0 | 49.0 | 2.2 | 1.6 |

*Scrollcase temperatures.

#### Other

Spring spill operation was initiated at 0001 hours on April 3.  Total river flow exceeded powerhouse capacity on April 27, 28, and 29 thus forcing spill.  Dissolved gas levels are reported through BPA and likely exceeded the 120% TDG gas cap.  The uniform spill pattern was used throughout this reporting week.

Inline Cooling Water Strainers: Cooling water strainers were inspected on May 2.  Six live juvenile lampreys and one steelhead were recovered.  Mortalities included 100 juvenile lampreys, 25 juvenile salmon, and 17 juvenile steelhead.

Invasive Species:There were no zebra mussels observed at the monitoring stations on April 8.

Piscivorous bird numbers have increased with gulls being the most common birds observed.  Activity has been focused in the tailrace and bypass outfall zones.  APHIS has been concentrating hazing efforts in these areas.  Pelican abundance has been low so far this season with observations primarily in the forebay.

Project:  Little Goose

# Biologists: George Melanson and Rick Weis

Dates: April 27 – May 3, 2012

## Turbine Operation

Turbine units 1 through 6 were available for service throughout this report period.  The turbine units were operated within the 1% efficiency criteria.

## Adult Fish Passage Facility

USACE and ODFW fisheries biologists performed measured inspections of the adult fishway April 27, 28, May 1 and 2.

Fish Ladder:  The ladder exit head differentials ranged between 0.0 and 0.4feet (criteria < 0.5 ft.).  Water depths over the weirs held steady at 1.2 feet (criteria 1.0-1.3 ft.) and picketed lead head differentials held steady at 0 feet (criteria < 0.3 ft.).  No debris was observed at the picketed leads or the ladder exit.  The air bubbler used to prevent debris from collecting near the ladder exit operated satisfactory.

Fishway Entrances and Collection Channel:  Channel to tailwater head differentials ranged between 1.4 and 1.8 feet (criteria 1.0 to 2.0 ft.).  SSE weir depths ranged between 8.1 and 8.6 feet (criteria ≥8.0 ft). NPE weirs rested on sill and depths ranged between 6.3 and 7.4 feet (criteria ≥7.0 ft or on sill).  NSE weirs remain at fixed elevations of 531.5 feet and depths ranged between 7.1 and 8.7 feet (criteria ≥ 6.0 ft.).  Collection channel surface water velocities (criteria 1.5 to 4.0 fps) ranged from 1.9 to 2.7 fps near the SSE and 2.0 to 2.7 fps near the NSE.

Auxiliary Water Supply System:  All fish pumps operated within criteria this report period.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Up to 1,600 square feet of scattered woody debris was observed inside the trash shear boom.  Little to no debris was observed outside the trash shear boom.

Spillway Weir:  The spillway weir operated in the low crest position.

ESBS/VBS:  All ESBS operated within criteria this report period.  Drawdown measurements across ESBS and VBS were performed on May 2.  All measurements indicated no debris buildup and screens in good operating criteria.

Orifices, Collection Channel, Dewatering Structure, Flume:  The juvenile collection system was operated throughout this period with 22 open orifices.

Transportation Facility:  The facility performed 24 hour (0700 to 0700 hrs.) secondary bypass operations on April 29 - 30 to collect fish for condition sampling.  The estimated collection totaled 388,963 smolts.  All fish were bypassed.  Descaling and mortality rate was 0.4% and less than 0.1% respectively.  The facility started collection for transport on May 3 at 0700 hours.

Transport Summary:  Daily barging transport operations at Little Goose are scheduled to begin with the first barge departing on May 4.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Little Goose Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 178.4 | 114.9 | 72.0 | 34.4 | 51.1 | 48.1 | 1.8 | 1.4 |

*Ladder temperature.

Other

Inline Cooling Water Strainers:  On May 3, all cooling water strainers were inspected.  There were 65 juvenile Lamprey and 10 unidentified smolts removed.  All were mortalities.

Invasive Species:  The Zebra Mussel substrate monitor was inspected on April 2.  No mussels were observed.  The next inspection is scheduled for May 7.

Avian Activity: Bird hazing by USDA continued this week.  Overall, piscivorous activity was minimal.

Project:  Lower Granite

# Biologist(s):  Mike Halter and Ches Brooks

Dates: April 27 – May 3, 2012

## Turbine Operation

Lower Granite had turbine units 1, 2, 3, 5 and 6 available for power generation at the beginning of the report period.  Turbine unit 4 is out of service for cavitation repair.  All turbine units (except unit 1) were operated within the 1% operation criteria.  Unit 1 turbine blades have been welded at a fixed angle and cannot achieve the 1% criteria.  This issue will be addressed after the spring freshet.

## Adult Fish Passage Facility

On April 27, 28, 29 and 30 the Lower Granite fisheries biologists performed measured inspections of the adult fishway system.

Fish Ladder:  The ladder weir depth at diffuser 14 was out of criteria during all inspections this report week with depths ranging from 0.8 to 0.9 feet (criterion 1.0 – 1.3 feet).  This condition was reported to the operators and the appropriate powerhouse personnel.

Fishway Entrances and Collection Channel:  Variable forebay and tailwater pool elevations during the week caused a few abnormal fishway readings in the report week.  Head differential readings remained within criteria at all adult fishway entrances during the weekly inspections, with the exception of the April 27 and April 29 inspections when the north powerhouse entrance was under criteria at 0.2 and 0.9 feet respectively (criterion 1.0 – 2.0 feet).  The low reading on April 27 was associated with an unusually high tailwater elevation of 638.2 feet.  Only north shore entrance 1 can adjust depth relative to the tailwater elevation North shore entrance 1 had not been adjusting its elevation adequately in auto mode to compensate relative to the fixed gate.  This issue was addressed by powerhouse crews on May 1 and 2, and though not reflected in this report, fishway conditions have improved.

Weir depths at the south shore fishway entrances met criteria during the weekly inspections.  The north powerhouse fishway entrances were on sill during the April 30 inspection due to tailwater elevations below 636.0 feet (these gates bottom out at elevations below 636.0 feet). North powerhouse fishway entrance weir depths were 7.6 feet on this date.  These gates were within depth criteria on all other inspections.  Weir depths at the north shore entrances ranged from 2.5 to 8.0 feet (criterion ≥ 7.0 feet).  North shore entrance 2 has been manually dogged off at 628.5 feet which is creating more weir depth than necessary at the loss of head differential.  As noted above, north shore entrance 1 has not been adjusting its elevation adequately in auto mode to compensate relative to the fixed gate.  A work request has been generated (and acted upon) to address this problem.  Normally weir depth readings at the north shore entrances are sacrificed in order to maintain the requisite 1.0 foot of head differential.

Velocity readings in the adult fishway collection channel transition pool area ranged from 0.94 to 1.13 feet per second and averaged 1.05 feet per second.

### Auxiliary Water Supply System:  Fish pumps 2 and 3 were operated during the week.  Fish pump 1 is out of service because of a potential bearing problem.  Fish pump 1 is expected to return to service during the next report week.

#### Juvenile Fish Passage Facility

As needed, fish were diverted to raceway 6 on April 30 and May 1-2 in support of NOAA-Fisheries Transport and Survival Studies.  All fish other than those needed for marking purposes and lab sample workup were diverted back to the river through the mid-river bypass pipe (secondary bypass) until May 1 at 0700 hours, when general collection into raceways began. The lab sample rate was 0.5% for the duration of the report week.

Forebay Debris/Gatewell Debris/Oil:  The amount of forebay debris varied during the week due to wind strength and direction; none was removed.

ESBSs/VBSs:  There were no problems with fish screens during the report week.  ESBS video inspections were last attempted on April 21, but were cancelled due to low water clarity.  The next inspections are scheduled for mid May.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  There were no problems with any of these structures during the week.  The debris load lightened considerably this week.  Orifices are again being backflushed every three hours around the clock to ensure they remain free of materials that might impact fish passage.

Transportation Facility:  General transport operations began with juvenile fish collection into raceways on May 1 at 0700 hours.  Everyday barging from Lower Granite started the next day.

Juvenile fish sampling activities began on March 25 and are scheduled to continue through October 31.

Transport Summary:  The first everyday barge left Lower Granite on May 2.  The final research barge of the season (index barging) departed Lower Granite on April 26.  Henceforth research fish will be barged weekly along with the regular fish collection.

Removable Spillway Weir:  Mandatory spill operations began at 0000 hours on April 3. The RSW was operated in support of general spill operations.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Granite Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 186.3 | 121.4 | 92.5 | 28.7 | 51.8 | 49.0 | 2.0 | 1.5 |

*Scrollcase temperature.

Other

Video counts in the adult fish ladder counting room began on March 1 and concluded on March 31.  Visual counting between the hours of 0400 and 2000 began on April 1.

Inline Cooling Water Strainers: Cooling water strainers were inspected for lamprey entrainment on April 30.  A total of 175 lamprey were found in the strainers over a combined run time of 3,956.4 unit hours.  The next cooling water strainer inspections are scheduled for late May.

Invasive Species:  The zebra mussel trap near the adult fishway exit was last examined for zebra mussels on April 15.  No evidence of zebra mussels was found.

Research

Adult Fish Trap Operations:  Adult fish trap operations continued with a sample rate of 10%.  Scale samples will be taken from one out of every 25 hatchery steelhead.  All wild steelhead captured will be PIT-tagged and scale and genetic samples taken.  Any previously PIT-tagged steelhead (either hatchery or wild) will have both scale and genetic samples taken for verification purposes.

Idaho Fish and Game (IDFG) Genetic Stock Identification: The goal of this study is to develop fine-scale genetic profiles for natural origin salmon and steelhead; develop genetic stock identification (GSI) techniques to estimate stock-specific escapement over LGR, monitor abundance, productivity and distribution of naturally produced adult and juvenile steelhead and salmon; research and monitor stock-specific life history characteristics. At LGR the goal of the study will be to enumerate and characterize the natural production of spring/summer Chinook salmon and steelhead above LGR with regards to age composition and genetic stock profiles. IDFG will sample every day until the first part of July with the goal to collect between 2,000-5,000 genetic samples each from yearling spring/summer chinook and steelhead and 500-3,000 genetic samples from subyearling fall chinook.

Nez Perce Tribal Fisheries Steelhead Kelt Research: The Nez Perce Tribal Fisheries in coordination with the Corps and The University of Idaho started steelhead kelt research work for the season this week at the holding tanks upstream of the main fish facility.   Clipped and unclipped kelts are being examined to determine the changes that occur during sexual maturity and to determine post spawning changes associated with successful downstream migration and recovery to spawn again.  Dependent on the group, steelhead kelts will be blood sampled, PIT-tagged, acoustic-tagged, trucked, barged, or returned back to the river.

NOAA-Fisheries Transport Study: NOAA staff PIT-tagged migrating smolts at the fish facility upstream raceways for their Transport Evaluation Study, in order to compare smolt to adult returns of in-river migrating smolts to the smolt to adult returns of transported smolts.  This week 13,242 clipped Chinook, 2,038 unclipped Chinook, 23,329 clipped steelhead, 1,603 unclipped steelhead, 43 unclipped sockeye and 194 coho were collectively, marked and transported or handled and transported.

NOAA-Fisheries Reach Survival Study: NOAA staff PIT-tagged smolts for their Survival Study to evaluate the in-river survival of juvenile salmonids bypassed into the tailrace at Lower Granite.  This week 1,647 unclipped yearling Chinook, 2,202 clipped steelhead and 2,119 unclipped steelhead were PIT-tagged and bypassed to the tailrace.