U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

#### FISH FACILITIES WEEKLY REPORT

#18-2012

# Project:  McNary

# Biologists: Carl Dugger and Bobby Johnson

Dates: June 29 – July 5, 2012

## Turbine Operation

McNary had 9 to 12 turbine units available for power generation this week.  All available turbine units operated within the 1% peak efficiency criteria this week.  Unit outages are recorded in Table 1.

Table 1.  Unit Outages at McNary Dam.

| Units | Outage Dates | Outage Length | Reason |
| --- | --- | --- | --- |
| 3 | Jun 4 to Jan 30. | 8 months. | Rewind contract. |
| 8 | Jun 11 to Jan 30. | 8 months. | Rewind contract. |
| 10 | Jun 29 to Jul 3. | 4.7 days. | Bearing issue resolved. |
| 11, 12 | Jun 29. | 10.5 hours. | Returned from transformer 6 testing. |

## Adult Fish Passage Facilities

On July 1, 3 and 4, the McNary fisheries biologist performed measured inspections of the adult fishways.  Visual fish counts and ladder exit water temperature monitoring continued.  Video monitoring of adult lamprey passage began July 1.

Weirs SFEW1, NFEW2 and NFEW3 are lowered daily from 2100 to 0400 hours in support of night time lamprey passage.  SFEW2 cannot be lowered as far this year as due to the newly installed lamprey passage stilts.    On July 2, a technician noted that SFEW2 had a slight amount of cable slack when in the lowered position.  The technical staff adjusted the weir the following day.  On July 2 and 3, a lamprey researcher installed cameras at SFEW1 and SFEW2.  With the camera frames in place, both weirs cannot be raised above 267.0 feet.  Fisheries technicians continue to monitor the weirs when the juvenile system is operating in primary bypass mode.

Fish Ladders:  Both ladders met all Fish Passage Plan criteria during measured inspections except on July 3 when the Washington ladder head over weir differential measured 0.8 feet.  This resulted in ladder flow oscillations.  The operators adjusted the exit weirs immediately.  Facility personnel are monitoring this exit more closely as debris along the north shore has increased.  The operators have flushed some of the debris down the navigation lock.  At the Oregon exit, the south traveling screen had multiple alarms which the operators reset.  In addition, the operators reset one wash pump alarm.  Screen differential monitoring revealed no problems.

Video cameras were installed this week at both (Washington and Oregon) count stations near the ladder exits in support of lamprey research.

Fishway Entrances and Collection Channel:  Spill turbulence and hydraulic gradients continue to make it difficult for the project to maintain entrance weir depth and calibration.  Some progress is being made – weirs are staying in calibration longer.

All Washington and most Oregon ladder inspection points were in criteria.   All week, the south powerhouse entrances, SFEW1 and SFEW2, measured weir depths ranging from 8.1 to 8.9 feet and 8.4 to 8.6 feet, respectively.  It is possible the stilts on SFEW2 are affecting the flow out of the south entrances.  The project was able to maintain the south pool differential at 1.0 to 1.1 feet.    Both SFEW1 and SFEW2 underwent scheduled on July 2.  All other Oregon inspection points were in criteria.  Collection channel velocities averaged 2.0 feet per second.

### Auxiliary Water Supply System:  For the week, fish pumps 1 and 3 operated with blade angles of 30 degrees with no interruptions in service.  Pump 2 remains out of service for major overhaul which will require a contract.  The juvenile facility continued to provide the usual 450 cfs to the north powerhouse pool.  The Wasco County PUD turbine had no interruptions in service this week.

#### Juvenile Fish Passage Facility

The spring-like bypass season continues with alternating days of primary and secondary bypass operations.  The switch between the 2 bypass modes takes place every morning at 0700 hours.  No deviation from this schedule occurred.  This week, 109,602 smolts and 20,700 juvenile lamprey were routed through the secondary bypass.

Forebay Debris/Gatewell Debris/Oil:  Forebay debris accumulations were light this week.  Most of the debris accumulated along the powerhouse.  The debris load did noticeably increase along the north shore and at the spillway.  Debris distribution is mainly affected by spillway configuration, turbine operations and weather.  A special debris spill lasting 1.8 hours took place on July 4 at night.  During this operation, 4 gates were raised and spill increased to 210 kcfs.  This action successfully removed the debris from the spill face.  The fisheries staff continued to monitor trash rack differentials and gatewell slots.  No unusual problems were found.

ESBSs/VBSs:  ESBSs are deployed in all turbine units except for unit 3 which is expected to remain out of service until January 2013.  The screen in slot 7C remains in transducer bypass mode.  No video camera inspections were conducted this week due to difficulties with the primary camera.  On July 10, the fishery staff plans to conduct a test inspection with a “snake” camera. No VBSs were found out of differential criteria this week.  Even so, a total of 9 screens were cleaned as a precautionary measure on June 29, July 3 and 5.  VBS rehabilitations continued.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe: This week, 42 orifices were in service.  No blockages were observed.  The transition screen cleaner remains out of service until a channel shutdown occurs, otherwise all automated systems operated satisfactorily.  The fisheries staff continued to monitor the channel during all shifts when in primary bypass mode and during VBS cleaning operations.

Transportation Facility:  During the “spring” bypass season, both bypass modes return all fish to the river.  PIT tag detection occurs in the full flow pipe during primary bypass operations and throughout the facility during secondary bypass operations.  Smolt monitoring occurs only during secondary bypass operations. The primary (A and B) PIT tag slide gates remained off and closed, until 0700 hours on June 30 when they were activated in support of the Pacific Northwest National Laboratory (PNNL) tag retention study (see below).  The system received scheduled maintenance this week.  The secondary (C and D) PIT/bypass gates were off and open.  Facility staff turns the sample gates off or on at 0700 hours each day so the gates will be functional only during secondary bypass operations.  Ice block checks of the return to river lines revealed no blockages.  However, due to the new location of the bypass outfall and high tailwater elevations, the fisheries staff is having difficulty seeing the ice blocks exit the pipe.

In preparation for the transport season, mechanics refurbished the barge loading boom, sample raceway release valves and the movable raceway flumes.  Technicians also cleaned and prepped the raceways.

On July 1, eleven juvenile lampreys were lost on the separator perforated plate during primary bypass operations.  The biologist reminded technicians to make sure the barrier screen is properly in place when the system is in primary bypass mode.

Transport Summary:  There is no fish transport in progress at this time.

River Conditions

River conditions during the week are outlined in Table 2 which summarizes data provided by the smolt monitoring staff.  The data day is from 0700 to 0700 hours.  The summer spill program calls for 50 percent of the total river flow to be passed as spill.  High flow conditions resulted in actual spill rates ranging from 58 to 72 percent of total river flow.  As mentioned above, a coordinated debris spill occurred on the night of July 4.  Routine water temperature monitoring efforts across the project began June 15.  This data is being reported separately.

Table 2.  River conditions at McNary Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF) |  | Water Clarity* (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 393.8 | 344.5 | 282.3 | 203.0 | 60.0 | 58.2 | 4.9 | 4.1 |

*Control room data.

Other

Inline Cooling Water Strainers:  Cooling water strainer inspections took place on July 3.  A total of 74 juvenile lamprey were recovered.  All but 5 of these were mortalities.  Ten smolt mortalities were also recovered from turbine unit 1.  Turbine units 3 and 8 were not examined as they are out of service until January, 2013.

Invasive Species:  The next zebra mussel trap examination will occur in late July.

Avian Activity:  Corps technicians continued bird counts.  Tailwater counts (exclusive of the bypass outfall) included 30 gulls, 25 terns and 55 pelicans.  Most birds were feeding in the spill area.  Pelicans are apparently feeding on adult shad along the navigation lock wing wall.  Pelicans are also occasionally feeding on carp and shad in powerhouse flow along the Oregon shore.  High counts at the bypass outfall included 15 gulls and 10 terns.

In forebay locations, an occasional tern, osprey, gull or pelican was observed.  In addition, pelicans, gulls and cormorants were seen on the rocks by the Washington shore boat dock.

No grebes were seen anywhere on project this week.

The bypass outfall water cannon remained out of service.  District personnel have contracted for the installation of a second pump to restore service.  The contract will also include outfall pipe walkway repairs.  APHIS continued hazing activities with two 8 hour shifts, which covers the 16 hours of day light typical this time of year.  The propane hazing cannons are operating well though strong winds do interrupt their operation.

Research:  Current onsite research includes the juvenile salmonid passage study, Gas Bubble Trauma (GBT) examinations, the adult lamprey passage study and ODFW angling efforts to sample Northern Pikeminnow and other fish species that prey on smolts.  The Oregon exit traveling screen study has been rescheduled for next year.

This week, PNNL researchers began utilizing the PIT tag sort by code system to recapture and evaluate tag loss rates of subyearling Chinook fitted with neutrally buoyant external JSAT tags.  Primary (A and B) PIT tag slide gates were activated at 0700 hours on June 30.  The first test fish were recovered on July 1.  These fish were subsequently examined the next day.

Project:  Ice Harbor

# Biologist:  Mark Plummer

Biological Technician:  Stephen Jeffers

Dates: June 29 – July 5, 2012

## Turbine Operation

Turbine units 1 – 6 were available for operation this reporting period.

## Adult Fish Passage Facilities

### Fish facility personnel inspected the adult fish passage ways on July 2, 3, and 5.

### Fish Ladders:  All north and south adult fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria. Channel/tailwater differential criterion is 1 – 2 feet.

### Fishway Entrances and Collection Channel (inspection date order):  The south shore entrance (SFE) was off sill with a depth of 8.0 feet, off sill with a depth of 7.6 feet, and off sill with a depth of 7.5 feet.  The north powerhouse entrance (NFE) was off sill with a depth of 10.2 feet, off sill with a depth of 8.7 feet, and off sill with a depth of 8.3 feet.  The north shore entrance (NSE) was off sill with a depth of 6.3 feet, off sill with a depth of 6.4 feet, and off sill with a depth of 5.8 feet.  The NSE and NFE are currently being operated in manual mode due to tailwater fluctuations caused by spill.  All out of criteria entrance weir depths and channel/tailwater differentials were reported to the shift operator for adjustment during the inspections.  The north shore entrance weir is indicating it is on sill, however measuring tape checks are indicating that the weir could still lower 1 foot.  A trouble report has been initiated and submitted to the electricians.  Fishway entrance criterion is 8 feet depth, greater than 8 feet depth, or on sill.  Channel/tailwater differential criterion is 1 – 2 feet.  Channel velocities readings ranged from 1.5 fps – 1.7 fps.  Channel velocity criterion is 1.5 fps – 4.0 fps.

### Auxiliary Water Supply System:  Two of the 3 north shore fish pumps were operated without problems.  All 8 south shore fish pumps were operated.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  No problems to report.  Fish ladder exits are clear of debris and the bubblers are operating satisfactory.

STSs/VBSs:  The STS are in continuous run mode due to the size of juvenile fish less than 120 mm at Lower Monumental Fish Facility as per the Fish Passage Plan (FPP).  Inspections are scheduled for July 16 and 18.

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe:  The juvenile fish bypass was placed into operation March 19, 20 orifices are open.  No problems to report.

Juvenile Bypass Facility:  The bypass was put into operation March 19.

Fish Sampling:  Juvenile fish sampling occurs Monday and Thursdays.

July 2:

| Species | Sampled | #Descaled | Morts | Avian Marks |
| --- | --- | --- | --- | --- |
| C-CH | --- | --- | --- | --- |
| UC-CH | --- | --- | --- | --- |
| C-CH-O | 5 | 1 | 0 | 0 |
| UC-CH-O | 11 | 0 | 0 | 0 |
| C-SH | 1 | 0 | 0 | 1 |
| UC-SH | --- | --- | --- | --- |
| C-COHO | --- | --- | --- | --- |
| UC-COHO | --- | --- | --- | --- |
| C-SOCK | --- | --- | --- | --- |
| UC-SOCK | --- | --- | --- | --- |
| TOTAL | 17 | 1 | 0 | 1 |

July 5:

| Species | Sampled | #Descaled | Morts | Avian Marks |
| --- | --- | --- | --- | --- |
| C-CH | --- | --- | --- | --- |
| UC-CH | --- | --- | --- | --- |
| C-CH-O | 5 | 0 | 0 | 0 |
| UC-CH-O | 45 | 2 | 0 | 0 |
| C-SH | 3 | 0 | 0 | 0 |
| UC-SH | 1 | 0 | 0 | 0 |
| C-COHO | --- | --- | --- | --- |
| UC-COHO | --- | --- | --- | --- |
| C-SOCK | --- | --- | --- | --- |
| UC-SOCK | --- | --- | --- | --- |
| TOTAL | 54 | 2 | 0 | 0 |

Removable Spillway Weir:  The RSW is in operation.  Spill for fish began April 3, 2012.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Ice Harbor Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 68.0 | 50.9 | 52.8 | 21.9 | 63 | 59 | 5.0 | 4.3 |

*Unit 1 scrollcase temperature.

Other

Inline Cooling Water Strainers:  Main turbine cooling water strainer inspections were performed June 19 and 20 during STS/VBS inspections.  A total of 4 juvenile lamprey mortalities were found.

Invasive Species:  No zebra mussels were observed during inspections.

# Project:  Lower Monumental

# Biologists: Bill Spurgeon and Elizabeth Lindsey

Dates: June 29 – July 5, 2012

## Turbine Operation

All available turbine units are being operated within the hard constraint of the 1% operation criteria.  Unit 6 was removed from service at 0730 hours on June 25 and remained out of service for annual maintenance through this period.  Unit 3 was out of service from 1035 hours on July 4 to 1350 hours on July 5 due to a loose exciter fan mount.

Adult Fish Passage Facility

The adult fishway was inspected by Corps and State biologists on June 29, 30, and July 1, 2, 3, 4, and 5.

Fish Ladders: Fishway exit head differentials and depths over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively) on all inspections.  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively) on all inspections.

### Fishway Entrances and Collection Channel:  NSE1 and NSE 2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections.  North shore channel/tailwater head was in criteria (1’-2’) on all inspections.

SPE 1 and SPE 2 weir gates were in sill criteria (criteria: > 8’ or on sill) on all inspections.  While on sill the gate depth readings were 6.9’, 6.0’, 7.0’, 7.1’, 6.8’, 6.3’, and 6.5 feet.  South powerhouse channel/tailwater head was in criteria (1’-2’) on all inspections.

SSE1 weir gate was in sill criteria (criteria: > 8’ or on sill) on all inspections.  While on sill the gate depth readings were 7.2’, 6.7’, 7.1’, 7.2’, 7.0’, 6.8’, and 6.3 feet.  SSE 2 was in criteria (6’ above sill) on all inspections.  South shore channel/tailwater head was in criteria (1’-2’) this week.

The collection channel velocity remained in criteria (1.5 - 4.0 ft/sec) this week.

### Auxiliary Water Supply System: All AWS pumps were in service and operating during this period.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 0.7 square yards of forebay debris observed during this period.  Gatewell debris ranged from 0-25% surface coverage.

STSs/VBSs:  STS operations remained in continuous run mode due to sockeye and Chinook under 120 mm in the sample.

Orifices, Collection Channel, Dewatering Structure, Flume:  The collection channel is operating with 20 orifices open.  The primary dewaterer automatic weirs were set to 528.1 feet and switched to the off position on June 18 to eliminate sudden water level fluctuations in the separator.

Collection Facility:  The facility is in collection mode for fish transport.

Transport Summary:  Every-other-day transport is occurring with barges departing on odd numbered days this month.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Monumental Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF)* |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 65.0 | 50.3 | 24.1 | 17.0 | 64.0 | 62.0 | 4.6 | 3.8 |

*Scrollcase temperatures.

#### Other

Summer spill operations were initiated at 0000 hours on June 21.

Inline Cooling Water Strainers:  Cooling water strainers were inspected on June 4.  No live lamprey was recovered.  Mortalities included 2 juvenile lampreys, 5 juvenile salmon, and 1 Siberian prawn.  About 3 dozen decomposed juvenile lampreys were removed from units 2 and 4 cooling water strainers.

Invasive Species: There were no zebra mussels observed at the monitoring stations on July 1.

Avian Activity: Piscivorous bird numbers remained very low this week.  Cormorants, gulls, and terns were the prominent species observed.  Hazing ended on June 2.

Research: Battelle research on fish passage and survival continued this week.

Project:  Little Goose

# Biologist: George Melanson

Dates: June 29 – July 5, 2012

## Turbine Operation

Turbine units 1 - 5 were available for service throughout this report period.  Turbine unit 6 was removed from service on July 1 at 0700 hours for annual maintenance and exciter replacement.  The turbine units were operated within the 1% efficiency criteria with one reportable excursion.  On June 29, turbine unit 1 operated outside the criteria from 0808 to 0826 hours.

## Adult Fish Passage Facility

USACE and ODFW fisheries biologists performed measured inspections of the adult fishway June 29, 30 and July 3.

Fish Ladder:  The ladder exit head differentials ranged between 0 and 0.1feet (criteria < 0.5 ft.).  Water depths over the weirs held steady at 1.2 feet (criteria 1.0-1.3 ft.) and picketed lead head differentials ranged between 0 and 0.1feet (criteria < 0.3 ft.).  No debris was observed at the picketed leads or at the ladder exit.  The air bubbler used to prevent debris from collecting near the ladder exit operated satisfactorily.

Fishway Entrances and Collection Channel:  Channel to tailwater head differentials ranged between 1.5 and 2.1 feet (criteria 1.0 to 2.0 ft.).  SSE weir depths ranged between 8.0 and 8.3 feet (criteria ≥8.0 ft). NPE weirs rested on sill and depths ranged between 5.2 and 5.8 feet (criteria ≥7.0 ft or on sill).  NSE weirs remain at fixed elevations of 531.5 feet and depths ranged between 5.7 and 6.3 feet (criteria ≥ 6.0 ft.).  Collection channel surface water velocities (criteria 1.5 to 4.0 fps) ranged from 1.7 to 2.1 fps near the SSE and 2.0 to 2.7 fps near the NSE.   On July 1, collection channel subsurface water velocity measured 2.62 fps (criteria 1.5 to 4.0) near the NPE.

Auxiliary Water Supply System:  All fish pumps operated within criteria this report period.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Nothing significant to report.

Spillway Weir:  The spillway weir operated in the high crest position.

ESBS/VBS:  All ESBSs operated within criteria this report period.  On July 5, drawdown measurements were performed on units 1 and 2.   All measurements indicated screens met good operating criteria.

Orifices, Collection Channel, Dewatering Structure, Flume:  The juvenile collection system operated satisfactorily throughout this period with 22 open orifices.

Transportation Facility:  The facility continued collection for transport.  Daily estimated collection ranged between 1,120 and 17,978, totaling 40,467 for the week.  All fish were transported except for 1 fry that was returned to the river.  Descaling and mortality rates for the period were 0.5% and 0.2% respectively.

Transport Summary:  All barging operations were satisfactorily completed.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Little Goose Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 65.8 | 49.1 | 30.7 | 17.8 | 63.9 | 62.5 | 5.6 | 4.6 |

*Ladder temperature.

Other

Inline Cooling Water Strainers:  Cooling water strainers were not inspected this week.  The last inspection occurred July 27 with 4 juvenile lamprey mortalities removed.

Invasive Species:  The zebra mussel substrate monitor was inspected on June 6.  No mussels were observed.  The next inspection is scheduled for July 8.

Avian Activity:   Piscivorous birds observed in the vicinity of the dam during the week included up to 21 seagulls, 15 cormorants and 1 tern.

Project:  Lower Granite

# Biologist(s):  Mike Halter and Ches Brooks

Dates: June 29 – July 5, 2012

## Turbine Operation

Lower Granite had turbine units 1, 2, 3, 5 and 6 available for power generation at the beginning of the report period.  Turbine unit 4 is out of service for cavitation repair.  All turbine units (except unit 1) were operated within the 1% operation criteria.  Unit 1 turbine blades have been welded at a fixed angle and cannot achieve the 1% criteria.  This issue will be addressed starting in July.

## Adult Fish Passage Facility

On June 30, July 1, and July 3 the Lower Granite fisheries biologists performed measured inspections of the adult fishway system.

Fish Ladder:   All criteria were met.  The differential between the forebay and the adult fish ladder exit was at 0.5 feet during the July 3 inspection (the maximum acceptable level).

Fishway Entrances and Collection Channel:  Head differential readings remained within criteria at the south shore and north powerhouse fishway entrances during the weekly inspections.  The head differential readings at the north shore fishway entrances were slightly out of criteria during the June 30 and July 3 inspections with a reading of 0.9 feet on both dates (criterion 1.0’ – 2.0’).  This was likely due to tailwater fluctuations caused by spill.

Weir depths at the south shore fishway entrances met criteria during all weekly inspections.  The north powerhouse fishway entrances were on sill on all inspections this week due to tailwater elevations below 636.0 feet (these gates bottom out at elevations below 636.0 feet).  North powerhouse fishway entrance weir depths ranged from 5.2 to 5.7 feet.  Weir depths at the north shore entrances ranged from 4.0 to 5.3 feet on the weekly inspections.  North shore weir depths are being sacrificed in order to maintain the requisite 1.0 foot of head differential.

Velocity readings in the adult fishway collection channel transition pool area ranged from 0.86 to 1.04 feet per second and averaged 0.97 feet per second during the weekly inspections.

### Auxiliary Water Supply System:  There were no problems with the auxiliary water system during the report week.   Fish pumps one and three were run all week.

#### Juvenile Fish Passage Facility

The last daily barge departed Lower Granite on May 28.  Every other day barging began on May 30 and fish barges will depart Lower Granite on the odd numbered days of the month during July.  The juvenile fish facility sample rate was increased from 4.0% to 10% at 0700 hours on June 30.   Due to a rapid drop off in fish numbers, the sample rate was increased again from 10% up to 25% at 0700 hours on July 5.

Forebay Debris/Gatewell Debris/Oil:  The amount of forebay debris varied during the week due to wind strength and direction; none was removed.

ESBSs/VBSs:  VBS/ESBS video inspections last took place on June 22 - 23.  All screens associated with turbine units were inspected and no problems were noted.  The next inspections are scheduled for mid July.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  Juvenile fish collection gallery orifices were backflushed at regular 3 hour intervals all week.  Debris levels were fairly light during the report week.

Transportation Facility:  The juvenile fish facility (JFF) operated smoothly during the week.  There were no operational problems of any kind with fish collection, fish sampling, or fish transportation equipment.  Avian hazing activities concluded for the season on June 30.

Due to the presence of juvenile lamprey in the raceways, lamprey friendly tail screens (with larger mesh openings) were deployed in all operating raceways on June 10 and remained in place during the report week.

Transport Summary:  The first every other day barge left Lower Granite on May 30.  The final research barge of the season (index barging) departed Lower Granite on April 26.  Research fish are now being barged along with the general fish collection.  Every other day fish barging operations have been going smoothly and are scheduled to continue through mid August.

Removable Spillway Weir:  Mandatory spill operations began at 0000 hours on April 3. The RSW continued to operated in support of general spill operations.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Granite Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 65.5 | 51.2 | 37.4 | 21.6 | 62.6 | 61.0 | 5.0 | 4.4 |

*Scrollcase temperature.

Other

Fish Counts: Visual adult fish counts at the adult ladder are taking place between 0500 and 2100 hours DST.  These fish counts began on April 1 and are scheduled to continue through October 31.  Video sockeye and lamprey counts from 2100 to 0500 hours DST were implemented on June 15.

Inline Cooling Water Strainers:  Cooling water strainers were last inspected for lamprey entrainment on June 27.  A total of 40 lamprey were found in the strainers over a combined run time of 2,320.9 unit hours.  The next cooling water strainer inspections are scheduled for late July.

Invasive Species:  The zebra mussel trap near the adult fishway exit was last examined for zebra mussels on June 7.  No evidence of zebra mussels was found.  The next inspection will take place on July 6.

Research

Adult Fish Trap Operations:  Adult fish trap operations continued with a sample rate of 10%.  Scale samples will be taken from one out of every 25 hatchery steelhead.  All wild steelhead captured will be PIT-tagged and scale and genetic samples taken.  Any previously PIT-tagged steelhead (either hatchery or wild) will have both scale and genetic samples taken for verification purposes.

Idaho Fish and Game (IDFG) Genetic Stock Identification:  The goal of this study is to develop fine-scale genetic profiles for natural origin salmon and steelhead; develop genetic stock identification (GSI) techniques to estimate stock-specific escapement over LGR, monitor abundance, productivity and distribution of naturally produced adult and juvenile steelhead and salmon; research and monitor stock-specific life history characteristics. At LGR the goal of the study will be to enumerate and characterize the natural production of spring/summer Chinook salmon and steelhead above LGR with regards to age composition and genetic stock profiles. IDFG will sample every day until the first part of July with the goal to collect between 2,000-5,000 genetic samples each from yearling spring/summer Chinook and steelhead and 500-3,000 genetic samples from subyearling fall Chinook.

United States Fish and Wildlife Service (USFWS), United States Geological Service (USGS), NMFS-Early Life History, migratory behavior and survival of fall Chinook salmon in the Snake River:  The goal of this study is to provide information to fishery managers to maximize the effectiveness of summer flow augmentation and understand how summer flow augmentation affects water temperature, water velocity, juvenile fall Chinook salmon migratory behavior, and juvenile fall Chinook salmon survival in Lower Granite Reservoir. The separation-by-code system at LGR will be used to recapture some of the fish PIT-tagged during beach seining to allow growth calculations and to photograph fish for morphological assessment.

Nez Perce Tribal Fisheries Steelhead Kelt Research: The Nez Perce Tribal Fisheries in coordination with the Corps and The University of Idaho concluded steelhead kelt research work for the season this week at the holding tanks upstream of the main fish facility.  Clipped and unclipped kelts were examined to determine the changes that occur during sexual maturity and to determine post spawning changes associated with successful downstream migration and recovery to spawn again.  Dependent on the group, steelhead kelts will be blood sampled, PIT-tagged, acoustic-tagged, trucked, barged, or returned back to the river.