U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

#### FISH FACILITIES WEEKLY REPORT

#33-2012

# Project:  McNary

# Biologists: Carl Dugger and Bobby Johnson

Dates: October 12 - 18, 2012

## Turbine Operation

McNary had eight to nine units available for power generation this report period.  No units ran outside the 1% efficiency operational criteria this week.  Unit outages are recorded in Table 1.

Table 1.  Unit Outages at McNary Dam.

| Units | Outage Dates | Outage Length | Reason |
| --- | --- | --- | --- |
| 3 | Jun 4 to Jan 30. | 8 months. | Rewind contract. |
| 8 | Jun 11 to Jan 30. | 8 months. | Rewind contract. |
| 11 and 12 | Sep 3 to Oct 25. | 3 months. | Install digital relay. |
| 14 | Sep 18 to Nov 24. | 2.25 months. | Turbine bearing/alignment. |
| 9 | Oct 15 to 18. | 3 days. | Annual maintenance. |
| 10 | Oct 16. | 22 minutes. | ESBS camera inspection. |

## Adult Fish Passage Facilities

On October 13, 15 and 16, the McNary fisheries biologist performed measured inspections of the adult fishways.  Visual fish counts continued.

Fish Ladders:  Both ladders met all Fish Passage Plan criteria during inspections.  Debris loads along the north shore remains low.  At the Oregon exit, screen differential monitoring revealed no problems.  One differential alarm occurred which the operators reset without incident.  Woody debris along the Oregon shore remains light and scattered with location dependant on wind direction.  Fisheries technicians are regularly checking picketed leads in both ladders for debris.

Fishway Entrances and Collection Channel:  All Washington ladder inspection points were in criteria.  Although entrance weirs met criteria, maintaining calibration has been difficult.  All week, the south powerhouse entrance weirs, SFEW1 and SFEW2, measured depths between 8.7 and 8.8 feet and 8.6 to 8.7 feet, respectively.  It is possible the stilts on SFEW2 are affecting the flow out of the south entrances.  The project was able to maintain the south pool differential at 1.4 feet.  All other Oregon ladder inspection points were in criteria.  Oregon ladder entrances remain in calibration.

Collection channel velocities averaged 1.0 feet per second.  The velocity meter remains out of the water due to a shortened cable.  Until this can be resolved, the fisheries crew will continue to measure surface velocity manually.

### Auxiliary Water Supply System:  For the week, fish pumps 1 and 3 operated with blade angles of 30 degrees with no interruptions in service.  Pump 2 remains out of service for major overhaul which will require a contract.  Project personnel plan to begin removing the pump on October 26.  The juvenile facility continues to provide the usual 450 cfs to the north powerhouse pool.  The Wasco County PUD turbine had no interruptions in service this week.

#### Juvenile Fish Passage Facility

Fall primary bypass season continues.  Light facility maintenance has begun.  Water (but no fish) continues to flow into the facility to avoid possible freeze breakage.

Forebay Debris/Gatewell Debris/Oil:  Forebay debris was very light and consisted of a mixture of wood and milfoil.  The debris distribution is mainly affect by wind direction.  The fisheries staff continued to monitor trash rack differentials and no discrepancies were found.  No trash racks were were cleaned this week and gatewell observations were satisfactory.

ESBSs/VBSs:  The project has ESBSs deployed in all turbine units except unit 3 which is out of service until January, 2013.  The screens in slots 1A, 1B and 7C slots remain in transducer bypass mode.  On October 16, ESBS camera inspections were conducted in turbines units 9 and 10 which revealed one problem.  The cleaning brush in slot 10B was missing the top 7’ of screen which operators subsequently reset.  Since Unit 9 was already out of service, no special outage was necessary for inspection.  ESBS rehabilitations continued with drive chains being replaced on spare ESBSs.  Although no out of criteria VBS differentials were found this week, the 12 VBSs associated with turbine units 10 through 13 were cleaned as a preventative measure on October 18.  Turbine unit 3 VBS slots continued to be used as staging areas during VBS swaps as the screens normally in this location are being rehabilitated.  As mentioned above, turbine unit 3 is out of service until January, 2013.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe: This week, 42 orifices were in use.   Because the ESBS rope in slot 7A was frayed, a biologist previously closed the slot’s south orifice and opened the north one.  Biologists continued to open and close orifices associated with units 3 and 8 as needed in support of VBS rehabilitation efforts (these units are out of service).  These changes are needed to maintain proper collection channel elevations.  All systems operated well in automatic mode.  The transition screen cleaning device remains out of service until a channel shutdown occurs.  The fisheries staff continues to monitor the collection channel 24 hour per day, 7 days per week, especially during VBS maintenance.

Transportation Facility:  Light maintenance is in progress.  The facility which remains watered up to avoid freeze breakage.  All other systems remain shutdown.  Smolt monitoring has ended for the season.  A contractor plans to continue work on the bypass walkway near the separator observation building the week of October 22.

Transport Summary:  Fish transport operations have ended for the season.

River Conditions

River conditions during the week are outlined in Table 2.  Reported data was compiled from COE websites and the control room.  The data day is from 0000 to 2400 hours.  No recordable spill occurred this week.  Scheduled spill way hoist maintenance continues.

Table 2.  River conditions at McNary Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 83.9 | 57.5 | 0.0 | 0.0 | 61.0 | 60.0 | 6.0 | 6.0 |

Other

Inline Cooling Water Strainers:  The next main unit cooling water strainer examination will occur in November.

Invasive Species:  The next zebra mussel trap examination will occur October 20.

Avian Activity:  Formal bird counts concluded for the season on September 30.  During fishway inspections, cormorants and groups of gulls are occasionally seen in the tailrace, most in the vicinity of the powerhouse, presumptively feeding on shad.  Groups of gulls were occasionally also seen at the bypass outfall.  An occasional gull, cormorant, pelican or small groups of grebes were seen in the forebay.  Gulls and cormorants also continued to roost on the rocks by the Washington shore boat dock.  At times, fairly large numbers of gulls were seen on or in the vicinity of these rocks.

The bypass outfall water cannon remained out of service.  Current plans are to install a second pump and complete walkway grating repairs during the late November to the end of December time period.

Research:  The adult lamprey passage study is now the only onsite research in progress.  This work is taking place only at the ladder exits.

Causal observations of the full flow flume revealed no problems with adult passage.

A November dive is planned for removal of below water equipment used for the juvenile passage study.

Project:  Ice Harbor

# Biologist:  Mark Plummer

Biological Technician:  Stephen Jeffers

Dates: October 12 - 18, 2012

## Turbine Operation

Turbine units 1-3 were available for operation this reporting period.  Turbine units 4-6 remain out of service.  Turbine units 5 and 6 are currently unwatered.

## Adult Fish Passage Facilities

### Fish facility personnel inspected the adult fish passage ways October 15, 17, and 18.

### Fish Ladders:  All north and south adult fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria.

### Fishway Entrances and Collection Channel (inspection date order):  The south shore entrance (SFE) was off sill with a depth of 7.6 feet, off sill with a depth of 7.6 feet, and off sill with a depth of 7.7 feet.  The north powerhouse entrance (NFE) was on sill with a depth of 7.7 feet, on sill with a depth of 8.7 feet, and on sill with a depth of 8.0 feet.  The north shore entrance (NSE) was off sill with a depth of 7.5 feet, off sill with a depth of 8.4 feet, and off sill with a depth of 7.9 feet.  Fishway entrance criterion is 8 feet depth, greater than 8 feet depth or on sill at 332.25’ elevation per the Fish Passage Plan.  Physical measurements during these inspections indicated fishway entrances that were out of criteria are off sill by 0.1 to 0.3 feet, however the computer readings indicate in criteria.  Channel/tailwater differential criterion is 1 – 2 feet.  Out of criteria inspection points are reported to the shift operator for adjustments.  Channel velocities readings were 3.1, 2.5, and 2.1 fps.  Channel velocity criterion is 1.5 fps – 4.0 fps.

### Auxiliary Water Supply System:  Two of the 3 north shore fish pumps were operated without problems.  Six of 8 south shore fish pumps were operated without problems.  South shore fish pump 4 remained out of service due to excessive gearbox oil leakage.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  No problems to report.  Fish ladder exits are clear of debris and the bubblers are operating satisfactorily.

STSs/VBSs:  The STS screens are in cycle run mode.  October STS/VBS inspections are tentatively scheduled for October 22 and 24.

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe:  The juvenile fish bypass was placed in operation March 19; twenty orifices are open.  No problems to report.

Juvenile Bypass Facility:  The bypass was placed into operation March 19.

Juvenile Fish Sampling:  The last sample of the 2012 season occurred July 12.

Removable Spillway Weir:  Spill for fish passage ended September 1.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Ice Harbor Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 25.9 | 11.8 | 0.0 | 0.0 | 62 | 61 | 7.0 | 6.1 |

*Unit 1 scrollcase temperature.

Other

Inline Cooling Water Strainers:  The next cooling water strainer inspections are scheduled to took place on October 22 and 24.

Invasive Species: No zebra mussels were observed during adult fishway inspections.

# Project:  Lower Monumental

# Biologists: Bill Spurgeon and Elizabeth Lindsey

Dates: October 12 - 18, 2012

## Turbine Operation

The units are being operated within the hard constraint 1% operational criteria.  Unit 4 was removed from service at 0945 hours August 13 for six year annual maintenance and remained out of service through this period.  Unit 1 was out of service from 0700-1117 hours on October 16 for underwater camera inspection of gatewell slot 1B to determine why the STS cannot be removed from the slot.

Adult Fish Passage Facility

The adult fishway was inspected by Corps and PSMFC/State biologists on October 13, 15, 16, and 18.

Fish Ladders: Fishway exit head differentials and depths over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively) during all inspections.  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively) on all inspections.

### Fishway Entrances and Collection Channel: NSE1 and NSE 2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections.  North shore channel/tailwater head was in criteria (1’-2’) on all inspections.

SPE 1 and SPE 2 weir gates were in sill criteria (criteria: > 8’ or on sill) on all inspections.  While on sill the gate depth readings were 7.1’, 7.3’, 7.1’, and 7.0 feet.  South powerhouse channel/tailwater head was in criteria (1’-2’) on all inspections.

SSE1 weir gate was in depth criteria (criteria: > 8’ or on sill) on all inspections.  SSE 2 was in criteria (6’ above sill) on all inspections.  South shore channel/tailwater head was in criteria (1’-2’) this week.

The collection channel velocity remained in criteria (1.5 - 4.0 ft/sec) this week.

### Auxiliary Water Supply System:  AWS pump 3 was out of service from 0740-1030 hours on October 17 due to the thrust pump failing to start following station service shift.  All AWS pumps were in service and operating for the remainder of this period.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 5.0 square yards of forebay debris observed during this period.  Gatewell debris ranged from 0-29% surface coverage.  No oil was observed in the gatewells this week.

STSs/VBSs:  STS operation remains in cycle run mode.  STSs were inspected on October 9, 10 and 11.   All screens passed inspection.

Orifices, Collection Channel, Dewatering Structure, Flume:  The collection channel is operating with 18-19 orifices open.  The primary dewaterer automatic weirs remain set at 528.2 feet.

Collection Facility:  The load and hold facility is in winter maintenance mode.

Transport Summary:  Transport operations ended with the October 1 truck departure.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Monumental Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF)* |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 23.2 | 12.1 | 0.0 | 0.0 | 61.5 | 61.0 | 5.0+ | 4.6 |

*Scrollcase temperatures.

#### Other

Inline Cooling Water Strainers:  Cooling water strainers were inspected on October 2.  No live lamprey were recovered.   Mortalities included 4 Siberian prawns and 9 juvenile shad.

Invasive Species: There were no zebra mussels observed at the monitoring stations on October 2.

Avian Activity:  Piscivorous bird numbers remained low this week.  Gulls, cormorants, and grebes were the prominent species observed.  Hazing ended on June 2.

Project:  Little Goose

# Biologist: George Melanson

Dates: October 12 - 18, 2012

## Turbine Operation

Turbine units 1, 3, 4 and 6 were available for service throughout this report period.  Unit 2 remained out of service for annual maintenance.  Unit 5 was placed out of service for exciter replacement on October 2.  All available turbine units were operated within the 1% efficiency criteria.

## Adult Fish Passage Facility

USACE and ODFW fisheries biologists performed measured inspections of the adult fishway on October 12, 15 and 16.

Fish Ladder:  The ladder exit head differentials held steady at 0 feet (criteria < 0.5 ft.).  Water depths over the weirs ranged between 1.2 and 1.3 feet (criteria 1.0-1.3 ft.) and picketed lead head differentials remained steady at 0 feet (criteria < 0.3 ft.).  No debris was observed at the picketed leads or the ladder exit.  The air bubbler used to prevent debris from collecting near the ladder exit operated satisfactorily.

Fishway Entrances and Collection Channel:  Channel to tailwater head differentials ranged between 0.8 and 1.4 feet (criteria 1.0 to 2.0 ft.).  SSE weir depths remained steady at 8.3 feet (criteria ≥8.0 ft). Depths for NPE1 ranged between 6.8 and 7.2 feet (criteria ≥7.0 ft or on sill). As a result of two pump operations and decreased channel to head differentials, NPE2 was closed on September 27. NSE weirs remain at fixed elevations of 531.5 feet and depths ranged between 7.3 and 7.6 feet (criteria ≥ 6.0 ft.).  Collection channel surface water velocities (criteria 1.5 to 4.0 fps) ranged from 0.7 to 1.4 fps near the SSE and 2.3 to 2.5 fps near the NSE.   On September 25, with two pump operation, the collection channel subsurface water velocity measured 2.2 fps (criteria 1.5 to 4.0) near the NPE.

Auxiliary Water Supply System:   On September 25 at 0645 hours, fish pump 3 was removed from service (unscheduled outage) to repair a water leak.  Following repairs fish pump 3 was unable to restart and remained out of service.   Troubleshooting to determine the problem with fish pump three is ongoing.  The operating two pumps were increased in RPM to make up additional water to the fish collection channel.  On September 27 at approximately 1800 hours, NPE 2 was raised and closed to increase channel to head differentials.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Up to 300 square feet of debris floated in front of the unit intakes.

Spillway Weir:  The weir was not operated this week.

ESBS/VBS:   All ESBSs operated within criteria during the report period.  Monthly manual testing of ESBSs showed all screens in working order on October 3.  Drawdown measurements across ESBS and VBS were performed on October 17.  All measurements met criteria.

Orifices, Collection Channel, Dewatering Structure, Flume:  The juvenile collection system was operated throughout this period with 18 open orifices.

Transportation Facility:  The facility continued collection for transport.  The facility is operating at 100% sample rate.  Smolt collection totaled 558 for the week.  Descaling and mortality rates for the period were 3.1% and 0.9% respectively.

Transport Summary: Little Goose transported fish on alternate days using the 1-ton pick-up and 300 gallon midi-tank.   Salt in small concentrations of approximately 1 g/L were added to the midi-tank water to treat potential Columnaris disease and reduce stress.  All trucking operations to the Bonneville Fish Facility were satisfactorily completed.   Up to 5 gulls and 20 cormorants were observed in the act of foraging near the fish facility flume outfall area after fish release and another 50 cormorants were observed roosting on the fume support structures.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Little Goose Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 23.8 | 12.1 | 0 | 0 | 62.7 | 62.2 | 6 | 5.8 |

*Ladder temperature.

Other

Inline Cooling Water Strainers:  All cooling water strainers were inspected on October 16.  No fish were observed.

Invasive Species:  The zebra mussel substrate monitor was inspected on October 9.  No mussels were observed.  The next inspection is scheduled for November 5.

Avian Activity:   Piscivorous birds observed in the vicinity of the dam during the week included up to 35 seagulls, 25 cormorants and 3 grebes.

Project:  Lower Granite

# Biologist(s):  Mike Halter and Ches Brooks

Dates: October 12 - 18, 2012

## Turbine Operation

Lower Granite had turbine units 2, 4 and 6 available for power generation at the beginning of the report period.  Turbine unit 5 is out of service for cavitation repair with an indefinite return to service date.  Turbine unit 3 is out of service for annual maintenance.  The tentative return to service date for this unit is November 2.  Turbine unit 1 was returned to service at 1150 hours on October 12, following the repair of an ESBS in slot 1C.   Turbine unit 2 was taken out of service on October 18 at 0801 hours in support of a gatewell dipping operation, the unit returned to service at 0920 hours the same day.

Because of elevated descaling rates (as outlined below) turbine units 2 and 3, as of September 18, are being respectively operated as first and second turbine units in priority and unit 1 has been placed in last on, first off priority.  All operating turbine units were run within the 1% operation criteria during the week.

## Adult Fish Passage Facility

On October 12-14 the Lower Granite fisheries biologists performed measured inspections of the adult fishway system.

Fish Ladder:  All criteria were met.  The differential between the forebay and the adult fish ladder exit was 0.3 feet on all inspections this week.

Fishway Entrances and Collection Channel:  Head differential readings remained within criteria at the south shore and north powerhouse fishway entrances during the weekly inspections.  The head differential reading at the north shore fishway entrances was slightly out of criteria on the October 12 and October 14 inspections with readings of 0.9 feet (criterion 1.0’ – 2.0’).

Weir depths at the south shore fishway entrances met criteria during all weekly inspections.  The north powerhouse fishway entrances were on sill on all inspections this week due to tailwater elevations below 636.0 feet (these gates bottom out at elevations below 636.0 feet).  North powerhouse fishway entrance weir depths ranged from 6.7 to 7.1 feet.  Weir depths at the north shore entrances ranged from 4.7 to 6.6 feet on the weekly inspections.  North shore weir depths are being sacrificed in order to maintain the requisite 1.0 foot of head differential.

Velocity readings in the adult fishway collection channel transition pool area ranged from 0.96 to 1.14 feet per second and averaged 1.06 feet per second during the weekly inspections.

### Auxiliary Water Supply System:  Fish pumps 1 and 3 were run without any problems until the morning of October 16.  At 0549 hours, fish pump 1 failed during a station service shutdown.  The problem was traced to a broken fuse on a motor management relay.  Unfortunately, the plant did not have a replacement fuse in stock.  The plant then switched out the bulkheads and put fish pump 2 back on line.  Fish pumps 2 and 3 were up and running at 1320 hours and normal adult fishway operations resumed.

#### Juvenile Fish Passage Facility

The juvenile fish facility sample rate remained at 100% during the report week.

Forebay Debris/Gatewell Debris/Oil:  The amount of floating forebay debris increased to approximately 650 square yards this week; none was removed.

ESBSs/VBSs:  VBS/ESBS video inspections last took place on August 24.  The next inspections are scheduled for late October.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  Juvenile fish collection gallery orifices were backflushed at regular 3 hour intervals all week.  Debris levels remained light at these points during the report week.

Status of Elevated Descaling Rates at Lower Granite:  During the report period a total of 1,907 fish were sampled for descaling – of these 71 were counted as descaled – for an average descaling rate of 3.72%.  The descaling rate for the last report period was 5.77%.  As a comparison during the same time period, the average descaling rate for the years 2006-2010 was 5.25% as compared to 4.66% in 2011.  The facility mortality rate was 0.42% for the report week.

In an effort to narrow down possible locations where descaling may be occurring, Lower Granite personnel conducted a small gatewell dipping operation on October 18 in conjunction with our smolt monitors.  Bulkhead slot 2A was dipped at 0833 hours and a second (unsuccessful, 2 smolts) dip at 0841 hours.  The original plan was to dip gatewells in slots 2A, 2B, and 2C but the basket material broke (unexpectedly) during the second dip in the first slot dipped (2A).  Nevertheless a total of 22 juveniles (21 unclipped subyearling Chinook, 1 rainbow trout) and two jack Chinook were obtained on these dips.  Given the relatively low numbers of fish being collected at the fish facility this collection was better than expected.

The smolt monitors anesthetized all juvenile fish and examined them for descaling.  The fish appeared to be in excellent condition and there were no observations of full descaling (20% or greater on a side) on any fish.  Three of the subyearling Chinook had partial descaling (5% to 19% on a side) and it appeared the descaling was on the low side of this spread.

All juvenile fish were transported back to the fish facility and released back to the river through the adult release pipe adjacent to the sample holding tank.  The two jack Chinook were not anesthetized and were released directly back to the forebay.

Transportation Facility:  Due to increasing numbers of jack Chinook passing through the separator bars and into the lab sample, the facility installed a smaller series of separator bars to screen the jacks out of the sample.  These bars have proven quite effective in previous years.  The JFF operated smoothly during the week.  Avian hazing activities concluded for the season on June 30.  The sample rate remained at 100% during the week.

Transport Summary:  Every other day fish barging operations concluded on August 16.   All fish barges have been returned to Lower Granite and are docked for maintenance work and winter storage.  Fish trucking operations began on August 18 using the pickup midi-tanker.  Collected fish numbers remained relatively low this week and well within the capacity of this transport vehicle.   Starting on September 5, Lower Granite began combined fish truck transport operations with Little Goose.  Combined transport operations with Little Goose concluded with the October 7 trip.

Removable Spillway Weir:  The RSW was operated in support of general spill operations during the season.  Mandatory spill operations in support of fish passage ended on August 31.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1:  River conditions at Lower Granite Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 25.8 | 14.6 | 0.0 | 0.0 | 61.0 | 60.2 | 4.5 | 4.2 |

*Scrollcase temperature.

Other

Visual adult fish counting at the adult ladder is taking place between the hours of 0400 and 2000.  Visual fish counts began on April 1 and are scheduled to continue through October 31.

Inline Cooling Water Strainers:  Cooling water strainers were last inspected for lamprey entrainment on September 25.  No lamprey mortalities were found in the strainers over a combined run time of 965.3 unit hours.  The next cooling water strainer inspections are scheduled for late October.

Invasive Species:  The zebra mussel trap near the adult fishway exit was last examined for zebra mussels on October 7.  No evidence of zebra mussels was found.  The next inspection is scheduled for early November.

Research

Adult Fish Trap Operations:  Adult fish trap operations continued with a sample rate of 15%.  Scale samples will be taken from one out of every 25 hatchery steelhead.  All wild steelhead captured will be PIT-tagged and scale and genetic samples taken.  Any previously PIT-tagged steelhead (either hatchery or wild) will have both scale and genetic samples taken for verification purposes.

Fall Chinook Transport:  Collection of adult fall Chinook for transport to Lyons Ferry Hatchery and the Nez Perce Hatchery at Cherry Lane continued during the week.   The Nez Perce are trucking fish on Saturday and Sunday and Lyon’s Ferry Hatchery is trucking fish Monday – Friday.  Chinook jacks are being collected during the week and trucked to Lyon’s Ferry on Mondays.  Trucking operations will continue into November (or until hatchery needs are met).

National Marine Fisheries Service (NMFS) Late Season Subyearling Fall Chinook Transportation:  NMFS staff began PIT-tagging subyearling fall Chinook taken from the sample on September 6. The objective of this study is to assess the survival and returns of late season trucked and in-river subyearling fall Chinook. Approximately 50% of the marked fish will be transported and 50% will be bypassed to the river, 24 hours after recovering from PIT-tagging.