U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

#### FISH FACILITIES WEEKLY REPORT

#34-2012

# Project:  McNary

# Biologists: Carl Dugger and Bobby Johnson

Dates: October 19 - 25, 2012

## Turbine Operation

McNary had 9 turbine units available for power generation this week.  All turbine units ran within the 1% operational criteria this week.  On November 1, the soft constraint one percent criterion will begin.  Unit outages are recorded in Table 1.

Table 1.  Unit Outages at McNary Dam.

| Units | Outage Dates | Outage Length | Reason |
| --- | --- | --- | --- |
| 3 | Jun 4 to Jan 30. | 8 months. | Rewind contract. |
| 8 | Jun 11 to Jan 30. | 8 months. | Rewind contract. |
| 11 and 12 | Sep 3 to Nov 2. | 3.25 months. | Install digital relay. |
| 14 | Sep 18 to Nov 24. | 2.25 months. | Turbine bearing/alignment. |
| 4, 5 and 6 | Oct 23. | 42 minutes. | ESBS camera inspection. |

## Adult Fish Passage Facilities

On October 19, 21 and 23, the McNary fisheries biologist performed measured inspections of the adult fishways.  Visual fish counts will conclude October 31.  Video monitoring and counts of adult fish will continue this winter from November 1 to February 28, when ladders are in service.

Fish Ladders:  Both ladders met all fish Passage Criteria during measured inspections.  Debris loads along the north shore remain low.  The backup spillway power supply was tested on October 23, from 0901 to 0922 hours, resulting in a power outage at the Washington ladder.  Following the outage, normal ladder operation resumed after operators cleared multiple alarms and adjusted weir set points.  At the Oregon exit, screen differential monitoring revealed no problems.  One differential and one wash pump alarm occurred this week.  Normal operations resumed in both cases after operators reset the alarm.  Woody debris along the Oregon shore remains light and scattered with its location dependent on wind direction.  Fisheries technicians are regularly checking picketed leads in both ladders for debris.

Fishway Entrances and Collection Channel:  Biologists found all Washington Ladder inspection points in criteria.  Though in criteria, the entrance weirs have been difficult to keep in calibration.

All week, the south powerhouse entrance weirs (SFEW1 and SFEW2) weir depths ranged from 7.8’ to 8.9’ and 8.5’ to 8.7’ feet, respectively.  It is possible the stilts on SFEW2 are affecting the flow out of the south entrances.  The project was able to maintain the south pool differential at 1.3 to 1.4 feet.  All other inspection points were in criteria.  The Oregon ladder entrances remain in calibration.

Collection channel velocities averaged 1.0 feet per second which is typical for low tailwater elevations.  The velocity meter remains out of the water due to a shortened cable.  Until this is resolved, the fisheries crew will continue to measure surface velocity manually.  A new velocity meter cable is on order.

### Auxiliary Water Supply System:  For the week, fish pumps 1 and 3 operated with blade angles of 30 degrees with no interruptions in service.  Pump 2 remains out of service for major overhaul which will require a contract.  On October 26, the project will begin removing bulkheads and COE staging equipment as pump repairs are not likely to begin in the near future.  The juvenile facility continues to provide the usual 450 cfs to the north powerhouse pool.  The Wasco County PUD had no interruptions in service this week.  The above mentioned power outage had no effect on PUD turbine unit operations.

#### Juvenile Fish Passage Facility

The fall primary bypass season continued and light facility maintenance has begun.  Water (but no fish) continues to flow into the facility to avoid possible freeze breakage

Forebay Debris/Gatewell Debris/Oil:  Forebay debris accumulations ranged from none to light, consisting of a mixture of wood and milfoil.  Debris distribution was affected mainly by wind direction.  The fisheries staff continued to monitor trash rack differentials.  No problems were found and no trash racks were cleaned.

On October 25, in slot 11C, facility staff observed what appeared to be oil.  Since the turbine unit was already out of service, orifices were closed to isolate the oil and absorbent booms were deployed.  Because ESBS gearbox oil was thought to be the most likely possible source for the sheen, project personnel replaced the ESBS in that slot.  No problem was found with the screen following removal.  Since no apparent source for the oil was identified, the biologist closed all orifices associated with unit 11.  The orifices will remain closed until the problem can be resolved.

ESBSs/VBSs:  ESBSs are deployed in all turbine units except unit 3 which is out of service into January, 2013.  The screens associated with slots 1A, 1B and 7C remain in bypass mode.  On October 23, ESBS camera inspections were conducted in units 4, 5 and 7 and no problems were found.  As mentioned above, the project replaced the screen at 11C slot on October 25.   ESBS rehabilitations continued with drive chains being replaced on spare ESBSs.

VBS differential measurements indicated one screen was out of criteria this week.  This screen and 3 others were cleaned on October 23 and 25.  Turbine unit 3 VBS slots continued to be used as staging areas during VBS swaps as the screens normally in this location are being rehabilitated.  As mentioned above, turbine unit 3 is out of service until January, 2013

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  This week, 42 orifices were in use with one problem observed.  On October 23, the ESBS rope was removed from the orifice inflow in slot 1B.  Because the ESBS rope at 7A slot is frayed, the slot’s south orifice is closed and the north one is opened.  Biologists continued to open and close orifices associated with units 3 and 8 as needed in support of VBS rehabilitation efforts (these units are out of service).  These changes are needed to maintain proper collection channel elevations.  All systems operated well in automatic mode.  The transition screen cleaning device remains out of service until a channel shutdown occurs.  This week, the fisheries maintenance staff conducted scheduled maintenance on the orifice valve operators and replaced orifice attraction light bulbs.  The fisheries staff continues to monitor the collection channel 24 hour per day, 7 days per week, especially during VBS maintenance.

Transportation Facility:  Light maintenance is in progress.  The facility which remains watered up to avoid freeze breakage.  All other systems remain shutdown.  Smolt monitoring has ended for the season.  This week, facility staff removed the perforated plate from the porosity control unit for rehabilitation. A contractor will return to continue work on the bypass walkway near the separator observation building on November 12.

Transport Summary:  Fish transport operations have ended for the season.

River Conditions

River conditions during the week are outlined in Table 2.  Reported data was compiled from COE websites and the control room.  The data day is from 0000 to 2400 hours.  No recordable spill occurred this week.  Scheduled spill way hoist maintenance continues.

Table 2.  River conditions at McNary Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 113.7 | 67.8 | 0.0 | 0.0 | 60.0 | 60.0 | 6.0 | 6.0 |

Other

Inline Cooling Water Strainers:  Cooling water strainer examinations will occur in November.

Invasive Species:  The zebra mussel trap was examined October 20.  No mussels were found.

Avian Activity:  Formal bird counts concluded for the season on September 30.  During fishway inspections, cormorants and groups of gulls are occasionally seen in the tailrace, most in the vicinity of the powerhouse, presumptively feeding on shad (which were also noted in the gatewell slots.  Small groups of gulls were also seen at the bypass outfall.  An occasional gull, cormorant, pelican or small groups of grebes were seen in the forebay.  Gulls also continued to roost on the rocks by the Washington shore boat dock.  Occasionally, rafts of gulls have been seen upstream and downstream of the project.

The bypass outfall water cannon remained out of service.  Current plans are to install a second pump and complete walkway grating repairs.  Repairs are tentatively scheduled to start on November 12.

Research:  The adult lamprey passage study continues at the ladders’ exits only.  In November, a dive will occur to remove the below water equipment used for the juvenile passage study.  Causal observations of the full flow flume revealed no problems with adult passage.

On November 25, a member of the Fisheries Field Unit trained our lead technician to enter avian data.

Project:  Ice Harbor

# Biologist:  Mark Plummer

Biological Technician:  Stephen Jeffers

Dates: October 19 - 25, 2012

## Turbine Operation

Turbine units 1-3 were available for operation this reporting period.  Turbine units 4-6 remain out of service.  Turbine unit 6 is currently unwatered.  Turbine units were taken out of service for short periods while STS inspections were performed October 22 and 24.

## Adult Fish Passage Facilities

### Fish facility personnel inspected the adult fish passage ways October 22, 23, and 25.

### Fish Ladders:  All north and south adult fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria.

### Fishway Entrances and Collection Channel (inspection date order):  The south shore entrance (SFE) was off sill at 332.4 feet measured elevation with a depth of 7.6 feet, off sill at 332.5 feet measured elevation with a depth of 6.2 feet, and off sill at 332.5 feet measured elevation with a depth of 6.6 feet.  The north powerhouse entrance (NFE) was on sill at 333.2 feet measured elevation with a depth of 7.8 feet, on sill at 332.2 feet measured elevation with a depth of 6.6 feet, and on sill at 332.2 feet measured elevation with a depth of 8.0 feet.  The north shore entrance (NSE) was on sill at 332.3 feet measured elevation with a depth of 7.6 feet, off sill at 332.4 feet measured elevation with a depth of 6.6 feet, and off sill at 332.5 feet with a depth of 6.7 feet.  Fishway entrance criterion is 8 feet depth, greater than 8 feet depth or on sill at 332.25 per the Fish Passage Plan.  Physical measurements during these inspections indicated fishway entrances that were out of criteria are off sill by .1 to .3 feet; however the computer readings indicate they are on low limit and in criteria.  Channel/tailwater differential criterion is 1 – 2 feet.  Out of criteria inspection points are reported to the shift operator for adjustments.  Channel velocities readings were 2.3fps, 3.0fps, and 2.8 fps.  Channel velocity criterion is 1.5 fps – 4.0 fps.

### Auxiliary Water Supply System:  Two of the 3 north shore fish pumps were operated without problems.  Six of 8 south shore fish pumps were operated without problems.  South shore fish pump 4 remained out of service due to excessive gearbox oil leakage.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  No problems to report.  Fish ladder exits are clear of debris and the bubblers are operating satisfactorily.

STSs/VBSs:  The STSs are in cycle-run mode.  No problems were found during the October STS/VBS inspections.  November inspections are tentatively scheduled for November 26 and 28.

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe:  The juvenile fish bypass was placed into operation March 19.  Twenty orifices are open.  No problems to report.

Juvenile Bypass Facility:  The bypass was put into operation March 19.

Juvenile Fish Sampling:  The last sample of the 2012 season occurred July 12.

Removable Spillway Weir:  Spill in support of fish passage ended September 1.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Ice Harbor Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 23.8 | 13.5 | 0.0 | 0.0 | 61 | 60 | 7.0 | 7.2 |

*Unit 1 scrollcase temperature.

Other

Inline Cooling Water Strainers:  Cooling water strainer inspections took place on October 22 and 24.  No lamprey were present.

Invasive Species:  No zebra mussels were observed during adult fishway inspections.

# Project:  Lower Monumental

# Biologists: Bill Spurgeon and Elizabeth Lindsey

Dates: October 19 - 25, 2012

## Turbine Operation

All turbine units are being operated within hard 1% operational constraint criteria.  Turbine unit 4 was out of service from 0945 hours August 13 to 1458 hours on October 23 for six year annual maintenance.  Unit 5 was removed from service at 0930 hours on October 22 in support of annual maintenance.

Adult Fish Passage Facility

The adult fishway was inspected by Corps biologists on October 22, 24, and 25.

Fish Ladders: Fishway exit head differentials and depths over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively) on all inspections.  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively) on all inspections.

### Fishway Entrances and Collection Channel: NSE1 and NSE 2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections.  North shore channel/tailwater head was in criteria (1’-2’) on all inspections.

SPE 1 and SPE 2 weir gates were in sill criteria (criteria: > 8’ or on sill) on all inspections.  While on sill the gate depth readings were 6.9’, 7.5’, and 7.8 feet.  South powerhouse channel/tailwater head was in criteria (1’-2’) on all inspections.

SSE1 weir gate was in depth or sill criteria (criteria: > 8’ or on sill) on all inspections.  While on sill the gate depth reading was 7.7 feet.  SSE 2 was in criteria (6’ above sill) on all inspections.  South shore channel/tailwater head was in criteria (1’-2’) this week.

The collection channel velocity remained in criteria (1.5 - 4.0 ft/sec) this week.

### Auxiliary Water Supply System:  AWS pumps were rotated out of service for scheduled maintenance on October 22.  All AWS pumps were in service and operating for the remainder of this period.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 30.0 square yards of forebay debris observed during this period.  Gatewell debris ranged from 0-25% surface coverage.  No oil was observed in the gatewells this week.

STSs/VBSs:  STS operations remain in cycle-run mode.  STSs were inspected on October 9, 10 and 11.   All screens passed inspection.

Orifices, Collection Channel, Dewatering Structure, Flume:  The collection channel is operating with 18-19 orifices open.

Collection Facility:  The load and hold facility is in winter maintenance mode.

Transport Summary:  Transport operations ended with the October 1 truck departure.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Monumental Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF)* |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 22.0 | 13.7 | 0.0 | 0.0 | 59.5 | 58.0 | 4.5 | 4.4 |

*Scrollcase temperatures.

#### Other

Inline Cooling Water Strainers:  Cooling water strainers were inspected on October 2.  No live lamprey were recovered.   Mortalities included 4 Siberian prawns and 9 juvenile shad.

Invasive Species: There were no zebra mussels observed at the monitoring stations on October 2.

Avian Activity:  Piscivorous bird numbers remained low this week.  Gulls, cormorants, and grebes were the prominent species observed.  Hazing ended on June 2.

Project:  Little Goose

# Biologist: George Melanson

Dates: October 19 - 25, 2012

## Turbine Operation

Turbine units 1, 3, 4 and 6 were available for service for throughout this report period.  Unit 2 remained out of service for annual maintenance.  Unit 5 was placed out of service for exciter replacement on October 2.  The turbine units were operated within the 1% efficiency criteria.

## Adult Fish Passage Facility

USACE and ODFW fisheries biologists performed measured inspections of the adult fishway on October 12, 15 and 16.

Fish Ladder:  The ladder exit head differentials held steady at 0 feet (criteria < 0.5 ft.).  Water depths over the weirs ranged between 1.2 and 1.3 feet (criteria 1.0-1.3 ft.) and picketed lead head differentials remained steady at 0 feet (criteria < 0.3 ft.).  No debris was observed at the picketed leads or the ladder exit.  The air bubbler used to prevent debris from collecting near the ladder exit operated satisfactorily.

Fishway Entrances and Collection Channel:  Channel to tailwater head differentials ranged between 0.8 and 1.4 feet (criteria 1.0 to 2.0 ft.).  SSE weir depths remained steady at 8.3 feet (criteria ≥8.0 ft). Depths for NPE1 ranged between 6.8 and 7.2 feet (criteria ≥7.0 ft or on sill). As a result of two pump operations and decreased channel to head differentials, NPE2 was closed on September 27. NSE weirs remain at fixed elevations of 531.5 feet and depths ranged between 7.3 and 7.6 feet (criteria ≥ 6.0 ft.).  Collection channel surface water velocities (criteria 1.5 to 4.0 fps) ranged from 0.7 to 1.4 fps near the SSE and 2.3 to 2.5 fps near the NSE.   On September 25, with two pump operation, the collection channel subsurface water velocity measured 2.2 fps (criteria 1.5 to 4.0) near the NPE.

Auxiliary Water Supply System:   On September 25 at 0645 hours, fish pump 3 was removed from service (unscheduled outage) to repair a water leak.  Following repairs, fish pump 3 was unable to restart and remained out of service.  Troubleshooting to determine the problem with fish pump 3 is ongoing.  The operating speeds of the remaining 2 pumps were increased (more RPMs) to provide additional water to the fish collection channel.  On September 27 at approximately 1800 hours, NPE 2 was raised and closed to increase channel to head differentials.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Up to 300 square feet of debris floated in front of the unit intakes.

Spillway Weir:  The weir was not operated this week.  Spill in support of fish passage ceased on September 1.

ESBS/VBS:   All ESBS screens operated within criteria during the report period.  Monthly manual testing of ESBS screens showed all screens in working order on October 3.  Drawdown measurements across ESBS and VBS were performed on October 17.  All measurements met criteria.

Orifices, Collection Channel, Dewatering Structure, Flume:  The juvenile collection system was operated throughout this period with 18 open orifices.

Transportation Facility:  The facility continued collection for transport.  The facility is operating at 100% sample rate.  Smolt collection totaled 558 for the week.  Descaling and mortality rate for the period was 3.1% and 0.9% respectively.

Transport Summary: Little Goose transported fish on alternate days using the 1-ton pick-up and 300 gallon midi-tank.   Salt in small concentrations of approximately 1 g/L were added to the midi-tank water to treat potential Columnaris disease and to reduce stress.  All trucking operations to the Bonneville Fish Facility were satisfactorily completed.   Up to 5 gulls and 20 cormorants were observed in the act of foraging near the fish facility flume outfall area after fish release and another 50 cormorants were observed roosting on the fume support structures.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Little Goose Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 23.8 | 12.1 | 0 | 0 | 62.7 | 62.2 | 6 | 5.8 |

*Ladder temperature.

Other

Inline Cooling Water Strainers:  All cooling water strainers were inspected on October 16.  No fish were observed.

Invasive Species:  The zebra mussel substrate trap was inspected on October 9.  No mussels were observed.  The next inspection is scheduled for November 5.

Avian Activity:   Piscivorous birds observed in the vicinity of the dam during the week included up to 35 seagulls, 25 cormorants and 3 grebes.

Project:  Lower Granite

# Biologist(s):  Mike Halter and Ches Brooks

Dates: October 19 - 25, 2012

## Turbine Operation

Lower Granite had turbine units 1, 2, 4 and 6 available for power generation at the beginning of the report period.  Turbine unit 5 is out of service for cavitation repair.  The tentative return to service date for this unit is March 13, 2013. Turbine unit 3 is out of service for annual maintenance.  The tentative return to service date for this unit is November 2.

Because of elevated descaling rates in past weeks, turbine units 2 and 3, as of September 18, are being respectively operated as first and second turbine units in priority and unit 1 has been placed in last on, first off priority.  All operating turbine units were run within the 1% operational criteria during the week.

## Adult Fish Passage Facility

On October 19, 21, and 25 the Lower Granite fisheries biologists performed measured inspections of the adult fishway system.

Fish Ladder:  All criteria were met.  The differential between the forebay and the adult fish ladder exit ranged from 0.3 – 0.4 feet on inspections this week.

Fishway Entrances and Collection Channel:  Head differential readings remained within criteria at the south shore and north powerhouse fishway entrances during the weekly inspections.  The head differential reading at the north shore fishway entrances was slightly out of criteria on the October 21 and October 25 inspections with readings of 0.9 feet (criterion 1.0’ – 2.0’).

Weir depths at the south shore and north powerhouse fishway entrances met criteria during all weekly inspections.  Weir depths at the north shore entrances ranged from 5.0 to 8.6 feet on the weekly inspections.  North shore weir depths are being sacrificed in order to maintain the requisite 1.0 foot of head differential.

Velocity readings in the adult fishway collection channel transition pool area ranged from 0.94 to 1.16 feet per second and averaged 1.03 feet per second during the weekly inspections.

### Auxiliary Water Supply System:  There were no problems with the auxiliary water system during the report week.   Fish pumps 2 and 3 were run all week.

#### Juvenile Fish Passage Facility

The juvenile fish facility sample rate remained at 100% during the report week.

Forebay Debris/Gatewell Debris/Oil:  The amount of floating forebay debris decreased to approximately 600 square yards this week; none was removed.

ESBSs/VBSs:  VBS/ESBS video inspections last took place on August 24.  The next inspections are scheduled for late October.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  Juvenile fish collection gallery orifices were backflushed at regular 3 hour intervals all week.  Debris levels remained light at these points during the report week.

Status of Descaling Rates at Lower Granite:  The facility descaling rate was 2.96% this week compared to 3.72% last week and is lower than the 2006-2010 average descaling of 4.93% for this time period.  The facility mortality rate was 0.85% for the report week.

Transportation Facility:  Due to increasing numbers of jack Chinook passing through the separator bars and into the lab sample, the facility installed a smaller series of separator bars to screen the jacks out of the sample.  These bars have proven quite effective.  The JFF operated smoothly during the week.  The sample rate remained at 100%.

Transport Summary:  Every other day fish barging operations concluded on August 16.   All fish barges have been returned to Lower Granite and are docked for maintenance work and winter storage.  Fish trucking operations began on August 18 using the pickup midi-tanker.  Collected fish numbers remained relatively low this week and well within the capacity of this transport vehicle.   Starting on September 5, Lower Granite began combined fish truck transport operations with Little Goose.  Combined transport operations with Little Goose concluded with the October 7 trip.  In order to address concerns of avian predation at the Bonneville fish truck release site, all fish were released at the Dalton Point boat ramp (approximate river mile 133) minimal avian activity has been noted at this site.

Removable Spillway Weir:  The RSW was operated in support of general spill operations during the season.  Mandatory spill operations in support of fish passage ended on August 31.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1:  River conditions at Lower Granite Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 23.3 | 15.4 | 0.0 | 0.0 | 60.2 | 58.0 | 4.3 | 3.9 |

*Scrollcase temperature.

Other

Visual adult fish counts at the adult ladder are taking place between the hours of 0400 and 2000.  Visual fish counts began on April 1 and are scheduled to continue through October 31.

Inline Cooling water Strainers:  Cooling water strainers were last inspected for lamprey entrainment on September 25.  No lamprey mortalities or live lamprey were found in the strainers over a combined run time of 965.3 unit hours.  The next cooling water strainer inspections are scheduled for late October.

Invasive Species:  The zebra mussel trap near the adult fishway exit was last examined on October 7.  No evidence of zebra mussels was found.  The next inspection is scheduled for early November.

Avian Activity:  Avian hazing activities concluded for the season on June 30.

Research

Adult fish trap Operations:  Adult fish trap operations continued with a sample rate of 15%.  Scale samples will be taken from one out of every 25 hatchery steelhead.  All wild steelhead captured will be PIT-tagged and scale and genetic samples taken.  Any previously PIT-tagged steelhead (either hatchery or wild) will have both scale and genetic samples taken for verification purposes.

Fall Chinook Transport:  Collection of adult fall Chinook for transport to Lyons Ferry Hatchery and the Nez Perce Hatchery at Cherry Lane continued during the week.   The Nez Perce are trucking fish on Saturday and Sunday and Lyon’s Ferry Hatchery is trucking fish Monday – Friday.  Chinook jacks are being collected during the week and trucked to Lyon’s Ferry on Mondays.  Trucking operations will continue into November (or until hatchery needs are met).

National Marine Fisheries Service (NMFS) Late Season Subyearling Fall Chinook Transportation:

NMFS staff began PIT-tagging subyearling fall Chinook taken from the sample on September 6. The objective of this study is to assess the survival and returns of late season trucked and in-river subyearling fall Chinook.  Approximately 50% of the marked fish will be transported and 50% will be bypassed to the river, 24 hours after recovering from PIT-tagging.