U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

#### FISH FACILITIES WEEKLY REPORT

#35-2012

# Project:  McNary

# Biologists: Carl Dugger and Bobby Johnson

Dates: October 26 – November 1, 2012

## Turbine Operation

McNary had 8 to 10 turbine units available for power generation this week.  On November 1, the soft 1% efficiency criterion began.  For the week, no units ran outside the hard or soft constraints except on November 1 when units 11 and 12 briefly operated outside the criterion in support of tests.  Turbine unit outages are recorded in Table 1.

Table 1.  Unit Outages at McNary Dam.

| Units | Outage Dates | Outage Length | Reason |
| --- | --- | --- | --- |
| 3 | Jun 4 to Jan 30. | 8 months. | Rewind contract. |
| 8 | Jun 11 to Jan 30. | 8 months. | Rewind contract. |
| 14 | Sep 18 to Nov 24. | 2.25 months. | Turbine bearing/alignment. |
| 9 | Oct 30, Oct 31 and Nov 1 to unknown. | 1.5 hours, 4.3 hours and unknown. | Thrust bearing oil, unit 11 and 12 relay testing then water in thrust bearing oil. |
| 11 and 12 | Sep 3 to Nov 1. | 3.25 months. | Relay testing. |
| 13 | Oct 30 and Oct 31 to Nov 1. | 11.6 hours and 16 hours. | Transformer and unit maintenance then headgate adjustment. |
| 1 and 7 | Oct 30. | 48 minutes. | ESBS camera inspection. |
| 10 | Oct 31. | 4.3 hours. | Unit 11 and 12 relay testing. |

## Adult Fish Passage Facilities

On October 26, 28 and 30, the McNary fisheries biologist performed measured inspections of the adult fishways.  On October 30, NOAA Fisheries personnel performed their last inspection of the year.  Visual fish counting concluded on October 31.  Video monitoring of fish passage will continue this winter from November 1 to February 28, except when the ladders are out of service for maintenance.  Because video review occurs at the Washington count station, the fisheries staff winterized the Oregon count station.

Fish Ladders:  Both ladders met all Fish Passage Plan criteria during inspections.  Debris loads along the north shore remains low.  At the Oregon exit, screen differential monitoring revealed no problems.  One differential alarm sounded this week.  Normal weir operation resumed after operators reset the alarm.  Woody debris along the Oregon shore remains light and scattered with its location dependant on wind direction.  Fisheries technicians are regularly checking picketed leads in both ladders for debris.

Fishway Entrances and Collection Channel:  All Washington ladder inspection points met criteria during inspections.  Though in criteria, the entrance weirs have been difficult to keep in calibration.

Most Oregon ladder inspection points met criteria this week.  All week, the south powerhouse entrance weirs, SFEW1 and SFEW2, measured depths ranging from 8.3’ to 8.6’ and 8.2’ to 8.6’ respectively.  It is possible the stilts on SFEW2 are affecting the flow out of the south entrances.  The project was able to maintain the south pool differential at 1.3 to 1.4 feet.  All other Oregon ladder inspection points were in criteria.   Oregon ladder entrances remain in calibration.  Collection channel velocities averaged 1.3 feet per second which is typical for low tailwater elevations.  The new velocity meter cable remains on order.

### Auxiliary Water Supply System:  For the week, fish pumps 1 and 3 operated with blade angles of 30 degrees with no interruptions in service.  Pump 2 remains out of service for major overhaul which will require a contract.  On October 26, the project personnel removed bulkheads and COE staging equipment as pump repairs are not likely to begin in the near future.  The juvenile facility continued to provide the usual 450 cfs to the north powerhouse pool.

### On October 30, the Wasco County PUD turbine unit had two interruptions in service totaling 70 minutes in duration.  Both of these outages were in support of transformer work at turbine units 13 and 14.  The bypass system performed well during these outages.

#### Juvenile Fish Passage Facility

The fall primary bypass season continued and light facility maintenance has begun.  Water (but no fish) continues to flow into the facility to avoid possible freeze breakage.

Forebay Debris/Gatewell Debris/Oil:  Forebay debris accumulations ranged from very light to light, consisting of a mixture of wood and milfoil.  Debris distribution was affected mainly by wind direction.  The fisheries staff continued to monitor trash rack differentials.  No problems were found and no trash racks were cleaned.

Gatewell observations revealed no new problems other than a slight amount of oil found in slot 12B.  Booms and absorbent pads successfully removed oil from this slot and in slot 11C (discovered on October 25 and mentioned in the previous report).

ESBSs/VBSs:  ESBSs are deployed in all turbine units except unit 3 which is out of service into January, 2013.  The screens associated with slots 1A, 1B and 7C remain in bypass mode.  The ESBS in slot 7C was observed “short cycling” on October 28.  The term “short cycling” means that the cleaning brush reverses direction before reaching the top or bottom of the ESBS.  Normal brush operation was restored after operators adjusted the limit set points.  ESBS camera inspections were conducted in units 1 and 7 on October 30 and no problems were found.  ESBS rehabilitations continued with drive chains being replaced on spare ESBSs.

All VBS differential measurements met criteria this week.  However, the project cleaned 4 screens on Ocotber 27 and 30 as a preventative measure.  On October 30, operators briefly shut down unit 2 when the VBS in slot 2A was lowered.  The VBSs in unit 2 have been difficult for the general maintenance crew to reset as the retainers require modification.   Turbine unit 3 VBS slots continued to be used as staging areas during VBS swaps as the screens normally in this location are being rehabilitated.  As mentioned above, turbine unit 3 is out of service until January, 2013.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe: This week, 42 orifices were in use with one problem observed.  From October 26 to 29, orifices at unit 11and 12 were closed in support of oil removal as mentioned above.  During this time, spares were opened in units 13 and 14.  On October 29, the technician on duty misunderstood biologist instructions and closed an orifice in slot 7A and opened a spare orifice in slot 11C.  Both orifices in slot 7A remained closed for 19 hours.  Immediately following the discovery of this error, both orifices in this slot were reopened for 1.5 hours to help evacuate fish.  Examination of the slot included an ESBS camera inspection.  No fish were lost other than juvenile shad.  The biologist again reviewed orifice procedures with the staff.

Because the ESBS rope at 7A slot is frayed, the slot’s south orifice is closed and the north one is opened.  Biologists continued to open and close orifices associated with units 3 and 8 as needed in support of VBS rehabilitation efforts (these units are out of service).  These changes are needed to maintain proper collection channel elevations.  All systems operated well in automatic mode.  The transition screen cleaning device remains out of service until a channel shutdown occurs.  This week, the fisheries maintenance staff continued scheduled maintenance on the orifice valve operators.  The fisheries staff continues to monitor the collection channel 24 hour per day, 7 days per week, especially during VBS maintenance.

Transportation Facility:  Light maintenance is in progress.  The facility which remains watered up to avoid freeze breakage.  All other systems remain shutdown.  Smolt monitoring has ended for the season.  On November 5, the contractor will return to continue work on the bypass walkway near the separator observation building.

Transport Summary:  Fish transport operations have ended for the season.

River Conditions

River conditions during the week are outlined in Table 2.  Reported data was compiled from COE websites and the control room.  The data day is from 0000 to 2400 hours.  On October 27, recordable spill in excess of powerhouse capacity occurred.

Table 2.  River conditions at McNary Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 117.7 | 103.4 | 4.1 | 0.0 | 56.0 | 55.0 | 6.0 | 6.0 |

Other

Inline Cooling Water Strainers:  The next main unit cooling water strainer examination will occur November 6.

Invasive Species:  The next zebra mussel trap examinations will occur in late November.

Avian Activity:  Formal bird counts concluded for the season on September 30.  This week, the lead technician entered avian data into electronic form.  During fishway inspections, cormorants and groups of gulls were seen in the tailrace,.  Most cormorants were seen roosting on the navigation lock wing wall.  Most gulls were seen roosting or feeding in the powerhouse flow, presumptively on juvenile shad (which were also noted in the gatewell slots).  Small groups of gulls were also seen at the bypass outfall.  Night herons have been observed near the juvenile fish facility.  An occasional gull was seen in the forebay.  Gulls also continued to roost on the rocks by the Washington shore boat dock.  Occasionally, rafts of gulls have been seen upstream and downstream of the project.

The bypass outfall water cannon remained out of service.  Current plans are to install a second pump and complete walkway grating repairs.  Repairs are tentatively scheduled to start on November 5.

Research:  The adult lamprey passage study has concluded.  From November 5 to 9, a dive will occur to remove the below water equipment used for the juvenile passage study.  Causal observations of the full flow flume revealed no problems with adult passage.

Project:  Ice Harbor

# Biologist:  Mark Plummer

Biological Technician:  Stephen Jeffers

Dates: October 26 – November 1, 2012

## Turbine Operation

Turbine units 1-3 were available for operation this reporting period.  Turbine units 5 and 6 remain out of service.  Turbine unit 6 was tested October 26 from 0652 hours to 1536 hours.  On October 31, turbine unit 1 was out of service for a short period (20 minutes) to clean juvenile shad out of the cooling water strainer.  Turbine unit 4 returned to service October 31 for a short period and then was taken out of service again.  Turbine unit 4 returned to service November 1 at 1504 hours.

## Adult Fish Passage Facilities

### Fish facility personnel inspected the adult fish passage ways October 29, 30, and 31.

### Fish Ladders:  All north and south adult fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria.  The north and south adult fish ladder picketed leads were raised November 1.

### Fishway Entrances and Collection Channel (inspection date order):  The south shore entrance (SFE) was off sill at 332.4 feet measured elevation with a depth of 7.3 feet, off sill at 332.5 feet measured elevation with a depth of 8.0 feet, and on sill at 332.2 feet measured elevation with a depth of 7.8 feet.  The north powerhouse entrance (NFE) was on sill at 332.3 feet measured elevation with a depth of 7.5 feet, on sill at 332.1 feet measured elevation with a depth of 8.5 feet, and on sill at 332.2 feet measured elevation with a depth of 7.8 feet.  The north shore entrance (NSE) was on sill at 332.3 feet measured elevation with a depth of 7.4 feet, off sill at 332.7 feet measured elevation with a depth of 8.0 feet, and on sill at 332.3 feet measured elevation with a depth of 7.6 feet.  Fishway entrance criterion is 8 feet depth, greater than 8 feet depth or on sill at 332.25 per the Fish Passage Plan.  Physical measurements during these inspections indicated fishway entrances that were out of criteria are off sill by 0.1 to 0.3 feet; however the computer readings indicate they are on low limit and in criteria.  Channel/tailwater differential criterion is 1 – 2 feet.  Out of criteria inspection points are reported to the shift operator for adjustments.  Channel velocities readings were 2.6fps, 2.5fps, and 2.7 fps.  Channel velocity criterion is 1.5 fps – 4.0 fps.

### Auxiliary Water Supply System:  Two of the 3 north shore fish pumps were operated without problems.  Six of 8 south shore fish pumps were operated without problems.  South shore fish pump 4 remained out of service due to excessive gearbox oil leakage.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  No problems to report.  Fish ladder exits are clear of debris and the bubblers are operating satisfactorily.

STSs/VBSs:  The STS screens are in cycle-run mode.  No problems were found during the October STS/VBS inspections.  November inspections are tentatively scheduled for the 19th and 21st.

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe:  The juvenile fish bypass was placed in operation March 19.  Twenty orifices are open.  The power supply cord for the screen cleaner is wearing and exposing individual wires.  The screen cleaner is being operated in manual mode on a limited basis until repairs can be made.

Juvenile Bypass Facility:  The bypass was placed into operation March 19.

Juvenile Fish Sampling:  The last sample of the 2012 season occurred July 12.

Removable Spillway Weir:  Spill for fish ended September 1.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Ice Harbor Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 32.2 | 15.6 | 1.3 | 1.3 | 59 | 58 | 7.2 | 6.4 |

*Unit 1 scrollcase temperature.

Other

Inline Cooling Water Strainers:  Routine cooling water strainer inspections last took place on October 22 and 24.  Although no lamprey were present, numerous juvenile shad mortalities were recovered.  Unit 1 was taken out of service for emergency cleaning October 31 as juvenile shad plugged the associated cooling water strainer.

Invasive Species: No zebra mussels were observed during adult fishway inspections.

# Project:  Lower Monumental

# Biologists: Bill Spurgeon and Elizabeth Lindsey

Dates: October 26 – November 1, 2012

## Turbine Operation

Units were operated within the 1% operation hard constraint criteria through October 31.  As of November 1, the units are being operated in the soft constraint of the 1% criteria.  Unit 5 was out of service for annual maintenance from 0930 hours on October 22 to 1310 hours on November 1.

Adult Fish Passage Facility

The adult fishway was inspected by Corps biologists on October 29, 30, and November 1.

Fish Ladders: Fishway exit head differentials and depths over the weirs were within criteria (<0.5’ and 1.0’-1.3’, respectively) on all inspections.  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively) on all inspections.  The adult counting season ended on October 31.  North ladder picketed leads were raised on November 1.  The mechanical crew has been requested to raise picketed leads at the south shore count station.  Crane service is required to raise south ladder picketed leads.  The mechanical crew will raise them as time permits.

### Fishway Entrances and Collection Channel: NSE1 and NSE 2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections.  North shore channel/tailwater head was in criteria (1’-2’) on all inspections.  SPE 1 and SPE 2 weir gates were in sill criteria (criteria: > 8’ or on sill) on all inspections.  While on sill the gate depth readings were 6.8’, 6.6’, and 6.6 feet.  South powerhouse channel/tailwater head was in criteria (1’-2’) on all inspections.

SSE1 weir gate was in depth or sill criteria (criteria: > 8’ or on sill) on all inspections with the exception of a 7.6 feet reading on October 29 due to the gate being raised in manual mode from the sill position for an unknown reason.  The gate was returned to the sill position immediately after the discrepancy was reported.  While on sill the gate depth readings were 7.6’ and 7.1 feet.  SSE 2 was in criteria (6’ above sill) on all inspections.  South shore channel/tailwater head was in criteria (1’-2’) this week.

The collection channel velocity remained in criteria (1.5 - 4.0 ft/sec) this week.

### Auxiliary Water Supply System: All AWS pumps were in service and operating during this period.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 236.7 square yards of forebay debris observed during this period.  Gatewell debris ranged from 0-40% surface coverage.  Gatewell slots 2B and 2C were dipped on October 31 (1 cubic yard of debris removed).  No oil was observed in the gatewells this week.

STSs/VBSs:  STS operation remains in cycle mode.  STSs were inspected on October 9, 10 and 11.   All screens passed inspection.

Orifices, Collection Channel, Dewatering Structure, Flume:  The collection channel is operating with 18-19 orifices open.

Collection Facility:  The load and hold facility is in winter maintenance mode.

Transport Summary:  Transport ended with the October 1 load.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Monumental Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF)* |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 30.0 | 16.8 | 0.0 | 0.0 | 57.0 | 57.0 | 4.6 | 4.1 |

*Scrollcase temperatures.

#### Other

Inline Cooling Water Strainers:  Cooling water strainers were inspected on October 2.  No live lamprey were recovered.   Mortalities included 4 Siberian prawns and 9 juvenile shad.

Invasive Species: There were no zebra mussels observed at the monitoring stations on November 1.

Avian Activity:  Piscivorous bird numbers remained low this week.  Gulls, cormorants, and grebes were the prominent species observed.  Hazing ended on June 2.

Project:  Little Goose

# Biologist: Richard Weis

Dates: October 26 – November 1, 2012

## Turbine Operation

Turbine units 1, 3, 4 and 6 were available for service for most of the report period.  Unit 2 remained out of service for annual maintenance.  Unit 5 was placed out of service for exciter replacement on October 2.  Unit 3 was forced out of service on October 27 for wicket gates that would not close. Unit 6 was forced out of service on October 28 with exciter problems. Unit 3 and 6 were returned to service on November 1 after repairs were completed.  The turbine units were operated within the 1% efficiency criteria.

## Adult Fish Passage Facility

ODFW fisheries biologists performed measured inspections of the adult fishway on October 26, and November 1.

Fish Ladder:  The ladder exit head differentials ranged between 0 and 0.1 feet (criteria < 0.5 ft.).  Water depths over the weirs held steady at 1.2 feet (criteria 1.0-1.3 ft.) and picketed lead head differentials held steady 0 feet (criteria < 0.3 ft.).  No debris was observed at the picketed leads or the ladder exit.  The air bubbler used to prevent debris from collecting near the ladder exit operated satisfactorily.

Fishway Entrances and Collection Channel:  Channel to tailwater head differentials ranged between 1.5 and 1.8 feet (criteria 1.0 to 2.0 ft.).  SSE weir depths ranged between 8.2 and 8.3 feet (criteria ≥8.0 ft). Depths for NPE1 ranged between 6.9 and 7.2 feet (criteria ≥7.0 ft or on sill). As a result of two pump operations and decreased channel to head differentials, NPE2 was closed on September 27. NSE weirs remain at fixed elevations of 531.5 feet and depths ranged between 7.4 and 7.6 feet (criteria ≥ 6.0 ft.).  Collection channel surface water velocities (criteria 1.5 to 4.0 fps) ranged from 1.4 to 1.7 fps near the SSE and 2.7 fps for both inspections near the NSE.

Auxiliary Water Supply System:   On September 25 at 0645 hours, fish pump 3 was removed from service (unscheduled outage) to repair a water leak.  Following repairs fish pump 3 was unable to restart and remained out of service.   Troubleshooting to determine the problem with fish pump three is ongoing.  The operating speeds of the remaining 2 pumps were increased (i.e.: increased RPM) to provide additional water to the fish collection channel.  On September 27, NPE 2 was raised and closed to increase channel to head differentials.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Up to 8,100 square feet of debris floated in front of the unit intakes.

Spillway Weir:  The weir was not operated this week.  Spill in support of fish passage ceased on September 1.

ESBS/VBS:  All ESBS screens operated within criteria during the report period.  Monthly manual testing of ESBS screens showed all screens in working order on October 3.  Drawdowns tests were not conducted during this report period.

Orifices, Collection Channel, Dewatering Structure, Flume:  The juvenile collection system was operated throughout this period with 18 open orifices.

Transportation Facility:  The facility continued collection for transport at 100% sample rate. Smolt collection totaled 1,738 for the week.  Descaling and mortality rate for the period was 4.0% and 0.2% respectively.  On October 31, the facility switched from collection for transport to primary bypass operations.  All fish are now being routed to the tailrace.

Transport Summary: Little Goose transported fish on alternate days using the 1-ton pick-up and 300 gallon midi-tank.   Salt in small concentrations of approximately 1 g/L were added to the midi-tank water to treat potential Columnaris disease and to reduce stress.  All trucking operations to Dalton Point were satisfactorily completed.  No birds were seen during release.  The last fish transport trip took place on October 31.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Little Goose Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 27.4 | 15.7 | 0 | 0 | 57.5 | 56.2 | 6.0 | 6.0 |

*Ladder temperature.

Other

Inline Cooling Water Strainers:  All cooling water strainers were inspected on October 29.  No fish were observed.

Invasive Species:  The zebra mussel substrate monitor was inspected on October 9.  No mussels were observed.  The next inspection is scheduled for November 5.

Avian Activity:  Piscivorous birds observed in the vicinity of the dam during the week included up to 51 seagulls, 19 cormorants and 2 grebes.

Project:  Lower Granite

# Biologist(s):  Mike Halter and Ches Brooks

Dates: October 26 – November 1, 2012

## Turbine Operation

Lower Granite had turbine units 1, 2, 4 and 6 available for power generation at the beginning of the report period.  Turbine unit 5 is out of service for cavitation repair.  The tentative return to service date for this unit is March 13, 2013. Turbine unit 3 is out of service for annual maintenance.  The tentative return to service date for this unit is November 2.  All operating turbine units were rotated out of service on October 26 in support of VBS/ESBS video inspections.  These inspections began at 0708 hours and were completed at 1550 hours.

Because of elevated descaling rates (as outlined below) turbine units 2 and 3, as of September 18, are being respectively operated as first and second turbine units in priority and unit 1 has been placed in last on, first off priority.   All operating turbine units were run within the 1% operational criteria during this report period.

## Adult Fish Passage Facility

On October 26, 29, and 30 the Lower Granite fisheries and PSMFC/State biologists performed measured inspections of the adult fishway system.  The October 26 inspection was conducted with the ODFW biologist from Little Goose Dam.

Fish Ladder:  All criteria were met.  The differential between the forebay and the adult fish ladder exit ranged from 0.3 – 0.4 feet during inspections this week.

Fishway Entrances and Collection Channel:  Head differential readings remained within criteria at the south shore and north powerhouse fishway entrances during the inspections.  The head differential readings at the north shore fishway entrances were out of criteria on all inspections with readings ranging from 0.6 - 0.9 feet (criterion 1.0’ – 2.0’).

Weir depths at the south shore and north powerhouse fishway entrances met criteria during all fishway inspections.  Weir depths at the north shore entrances ranged from 5.0 to 8.6 feet on the weekly inspections.  North shore weir depths are being sacrificed in order to maintain the requisite 1.0 foot of head differential.  Velocity readings in the adult fishway collection channel transition pool area ranged from 0.91 to 1.08 feet per second and averaged 0.99 feet per second during the weekly inspections.

### Auxiliary Water Supply System:  There were no problems with the auxiliary water system during the report week.   Fish pumps 2 and 3 were run all week.

#### Juvenile Fish Passage Facility

The juvenile fish sample rate remained at the 100% until 0700 hours on October 31 when the system was switched to secondary bypass (all juvenile fish routed out the pipe to mid-river release).  This routing provides continued PIT-tag interrogation.  Weather permitting, this mode of operation will continue until December 15.

Forebay Debris/Gatewell Debris/Oil:  The amount of floating forebay debris increased to approximately 850 square yards this week; none was removed.

ESBSs/VBSs:  ESBS video inspections took place on October 26 and four of the screens in units 2, 4 and 6 had issues with either missing rivets or loose straps with sticks behind them.  These problems will be addressed as soon as possible.  The next inspections are scheduled for late November.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  Juvenile fish collection gallery orifices were backflushed at regular 3 hour intervals all week.  Debris levels remained light at these points during this report period.

Status of Descaling Rates at Lower Granite:  The facility descaling rate was 3.61% during the report period, compared to 2.96% last week and is slightly lower than the 2006-2010 average descaling of 3.88% for this time period.  The facility mortality rate was 1.05% for the report week.

Transportation Facility:  Due to increased numbers of jack Chinook passing through the separator bars and into the lab sample, the facility staff installed a smaller series of separator bars to screen the jacks out of the sample.  These bars have proven quite effective.  The JFF operated smoothly during the week.  The sample rate remained at 100% until 0700 hours on October 31.

Transport Summary:  The juvenile fish sample rate remained at the 100% level until 0700 hours on October 31 when the system was switched to secondary bypass (all juvenile fish routed out the pipe to mid-river release).  The system will operate in that mode through December 15.  The last fish transport truck left Lower Granite the morning of October 31.  Due to a relatively large increase in juvenile fish numbers, the semi-truck and trailer was utilized on this final trip.  Lower Granite also picked up fish at Little Goose that were in excess of their midi tanker truck’s capacity.  In order to address concerns of avian predation at the Bonneville fish truck release site, all fish were released at the Dalton Point boat ramp (approximate river mile 133); minimal avian activity has been noted at this site.

Removable Spillway Weir:  The RSW was operated in support of general spill operations during the season.  Mandatory spill operations in support of fish passage ended on August 31.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1:  River conditions at Lower Granite Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 29.1 | 16.8 | 0.0 | 0.0 | 57.7 | 55.9 | 4.7 | 4.1 |

*Scrollcase temperature.

Other

Visual adult fish counts continued between the hours of 0400 and 2000 until October 31 when visual counts ended for the season.  Video fish counting began November 1.

Inline Cooling Water Strainers: Cooling water strainers were inspected for lamprey entrainment on October 29.  No lamprey mortalities were found in the strainers over a combined run time of 1,032.6 unit hours.  The next cooling water strainer inspections are scheduled for late November.

Invasive Species:  The zebra mussel trap near the adult fishway exit was last examined on October 7.  No evidence of zebra mussels was found.  The next inspection is scheduled for early November.

Avian Activity: Avian hazing activities concluded for the season on June 30.

Research

Adult Fish Trap Operations: Adult fish trap operations continued with a sample rate of 15%.  Scale samples will be taken from one out of every 25 hatchery steelhead.  All wild steelhead captured will be PIT-tagged and scale and genetic samples taken.  Any previously PIT-tagged steelhead (either hatchery or wild) will have both scale and genetic samples taken for verification purposes.

Fall Chinook Transport:  Collection of adult fall Chinook for transport to Lyons Ferry Hatchery and the Nez Perce Hatchery at Cherry Lane continued during the week.   The Nez Perce are trucking fish on Saturday and Sunday and Lyon’s Ferry Hatchery is trucking fish Monday – Friday.  Chinook jacks are being collected during the week and trucked to Lyon’s Ferry on Mondays.  Trucking operations will continue into November (or until hatchery needs are met).

National Marine Fisheries Service (NMFS) Late Season Subyearling Fall Chinook Transportation:  NMFS staff began PIT-tagging subyearling fall Chinook taken from the sample on September 6. The objective of this study is to assess the survival and returns of late season trucked and in-river subyearling fall Chinook. Approximately 50% of the marked fish will be transported and 50% will be bypassed to the river, 24 hours after recovering from PIT-tagging.  The PIT-tagging and trucking portion of this study concluded on October 31.