U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

#### FISH FACILITIES WEEKLY REPORT

#38-2012

# Project:  McNary

# Biologists: Carl Dugger and Bobby Johnson

Dates: November 16 - 22, 2012

## Turbine Operation

McNary had 11 turbine units available for power generation this week.  On November 1, the soft one percent criterion began.  At times, units ran outside the criteria at BPA’s request.   Unit outages are recorded in Table 1.

Table 1.  Unit Outages at McNary Dam.

| Units | Outage Dates | Outage Length | Reason |
| --- | --- | --- | --- |
| 3 | Jun 4 to Jan 30. | 8 months. | Rewind contract. |
| 8 | Jun 11 to Jan 30. | 8 months. | Rewind contract. |
| 14 | Sep 18 to Dec 22. | 3.25 months. | Turbine bearing/alignment. |
| 10 | Nov 19. | 7 hours. | High thrust bearing temp. |
| 2 & 13 | Nov 20. | 29 minutes. | ESBS camera inspection. |

## Adult Fish Passage Facilities

On November 16, 18 and 21, the McNary fisheries biologist performed measured inspections of the adult fishways.  Video counts and monitoring of adult passage is in progress.  Video counts and monitoring will continue through February 28, except when the ladders out of service for winter maintenance. Fisheries technicians are regularly checking picketed leads in both ladders for debris.

Fish Ladders:  Both ladders met all Fish Passage Plan criteria during measured inspections except on November 16 and 21.  On those dates, the Washington ladder count station differential measured 0.7 and 0.6 feet respectively due to debris on the picketed leads.  Satisfactory differentials were restored after the picketed leads were cleaned.  On November 18, the Washington ladder head over weir differential measured 1.4 feet, possibly due to set points needing adjustment.  On November 20, all Washington ladder exit weirs underwent scheduled maintenance.  During this scheduled maintenance, the upper limit switch on weir 335 failed, which forced exit weir set point adjustments.  The limit switch has not yet been replaced.

Traveling screen differential measurements at the Oregon ladder exit have been satisfactory.  However, there were multiple traveling screen alarms which the operators reset without incident.    On November 18, all Oregon exit weirs triggered alarms which the operators also reset without incident.  The same day, the Oregon ladder head over weir differential measured 1.4 feet, possibly due to set points requiring adjustments.  Operators successfully adjusted the set points later in the day, restoring the desired differentials.

Fishway Entrances and Collection Channel:  The biologist found all Washington ladder inspection points in criteria.  However, on November 18, the biologist noticed that the entrance weirs appeared to not have moved.  A comparison with past inspection records revealed that the weirs had not moved since November 2.  On November 19, project maintenance personnel resolved the issue and calibrated the weirs.

All week, the south powerhouse entrance weirs, SFEW1 and SFEW2, measured depths of 8.3 to 8.4 feet and 8.2 to 8.6 feet, respectively.  It is possible the stilts on SFEW2 are affecting the flow out of the south entrances.  The project was able to maintain the south pool differential between 1.0 and 1.4 feet.  On November 18 and 21, the north powerhouse pool differential respectively measured 0.8 to 0.9 feet.   Also, on November 18, NFEW2 and NFEW3 weir depths each measured 8.9 feet.  North powerhouse readings are likely being affected by the juvenile system being in emergency bypass mode.  Collection channel velocities averaged 1.6 feet per second.  The new velocity meter cable remains on order.

### Auxiliary Water Supply System:  For the week, fish pumps 1 and 3 were operated with blade angles of 30 degrees with no interruptions in service.  Pump 2 remains out of service for major overhaul which will require a contract.  The juvenile facility remains in emergency bypass and is no longer providing the usual 450 cfs to the north powerhouse pool.  The Wasco County PUD turbine unit had no interruptions in service this week.

#### Juvenile Fish Passage Facility

Fall bypass season continues with the system in emergency bypass due to failure of the rectangular screen cleaning device in the collection channel.  The staff continued light maintenance at the facility which has been dewatered and winterized to avoid possible freeze breakage.

Forebay Debris/Gatewell Debris/Oil:  Forebay debris was light, consisting of a mixture of wood and milfoil.  Debris distribution is mainly affected by wind direction.  The fisheries staff continued to monitor trash rack differentials and no problems were found.  No racks were cleaned.  Gatewell observations produced satisfactory results.

ESBSs/VBSs:  ESBSs are deployed in all turbine units except unit 3 which is out of service until January, 2013.  The screens in slots 1A, 1B and 7C remain in transducer bypass mode.  The ESBS in slot 7C was observed “short cycling” on November 21.  The term “short cycling” means that the cleaning brush reverses direction before reaching the top or bottom of the ESBS.  Normal brush operation was restored after operators adjusted the limit set points.  ESBS camera inspections took place in turbine units 2 and 13 this week.  All inspected screens were found in satisfactory condition.  ESBS rehabilitations continued.  The fisheries staff continued to monitor VBS differentials.  Three screens were found out of criteria during higher electrical loads.  These and one other screen were cleaned on November 16, 17 and 21.  On November 16 and 17, two damaged VBSs stored in unit 3 were removed and 3 rehabilitated screens were installed in anticipation of unit testing in December (the third screen slot was empty).

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe: This week, 42 orifices were in use and no problems were observed.  Because the ESBS rope in slot 7A is frayed, the slot’s south orifice remains closed and the north one is open.  Orifice valve operators underwent scheduled maintenance this week.  The fisheries staff continued to monitor orifices when on shifts.

Emergency bypass continues with all systems out of service.  This week, maintenance staff determined that the replacement rectangular dewatering screen clutch will require custom fabrication in Japan.  The earliest possible delivery date for this part is December 13.  Electricians serviced the collection channel stairwell lighting this week.  Stairwell lighting has been inoperative for several years.

Transportation Facility:  Scheduled facility maintenance continued.  All systems remain shutdown.  Smolt monitoring has ended for the season.  Work continued on the bypass line access walkway near the separator.  Project welders will begin rebuilding the porosity control screens next week.

Transport Summary:  Fish transport operations have ended for the season.

River Conditions

River conditions during the week are outlined in Table 2.  Reported data was compiled from COE websites and the control room.  The data day is from 0000 to 2400 hours.

Table 2.  River conditions at McNary Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 150.3 | 94.1 | 0.0 | 0.0 | 52.0 | 52.0 | 6.0 | 5.4 |

Other

Inline Cooling Water Strainers:  The next main unit cooling water strainer examinations will occur in early December.

Invasive Species:  On November 18, facility staff noted that both zebra mussel detection traps were missing.  The stations were replaced on November 20.

Avian Activity:  Formal bird counts concluded for the season on September 30.  During fishway inspections, cormorants and groups of gulls were seen in the tailrace.  Most cormorants were seen roosting on the navigation lock wing wall.  The gulls were also roosting or feeding in the powerhouse flow.  An occasional merganser was also observed in the tailrace.  Bird numbers appear to be fluctuating with the outgoing juvenile shad migration.  Small groups of gulls and cormorants continued to be seen at the emergency bypass outfall.  Forebay observations included an occasional gull, groups of grebes and occasional cormorants.  No birds were observed roosting on the rocks by the Washington shore boat dock this week.

The bypass outfall water cannon remained out of service.  Contractor personnel are currently repairing walkway gratings.  Pump installation will follow the walkway grating repairs.

Research:  No on site research is in progress at this time.

Project:  Ice Harbor

# Biologist:  Mark Plummer

Biological Technician:  Stephen Jeffers

Dates: November 16 - 22, 2012

## Turbine Operation

Turbine units 1, 2, 3, and 4 were available for operation this reporting period.  Turbine unit 3 returned to service November17 at 1530 hours.  Turbine units 5 and 6 remain out of service.  Turbine units 2 and 4 were out of service November 19 to clean turbine unit cooling water strainers.  Turbine unit 1 went out of service for a short period November 21, also to clean the turbine cooling water strainers.  The strainers had become plugged with juvenile shad.  Turbine units 2 and 3 went out of service for short periods November 21 in support of STS inspections.

## Adult Fish Passage Facilities

### Fish facility personnel inspected the adult fish passage ways November 19, 20, and 21.

### Fish Ladders:  All north and south adult fish ladder inspection areas (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria.  The north and south adult fish ladder picketed leads were raised November 1.

### Fishway Entrances and Collection Channel (inspection date order):  The south shore entrance (SFE) was on sill with 8.20 feet depth, off sill with 8.1 feet depth, and on sill with 6.7 feet depth. The north powerhouse entrance (NFE) was on sill with 8.3 feet depth, on sill with 9.1 feet depth, and on sill with 6.6 feet depth. The north shore entrance (NSE) was on sill with 8.4 feet depth, off sill with 8.8 feet depth, and on sill with 6.7 feet depth.  Fishway entrance criterion is 8 feet depth, greater than 8 feet depth or on sill at 332.25 per the Fish Passage Plan.  Channel/tailwater differential criterion is 1 – 2 feet.  Out of criteria inspection points are reported to the shift operator for adjustments.  Channel velocities readings were 2.6 fps, 2.4 fps, and 3.1 fps.  Channel velocity criterion is 1.5 fps – 4.0 fps.

### Auxiliary Water Supply System:  Two of the 3 north shore fish pumps were operated without problems.  Six of 8 south shore fish pumps were operated without problems.  South shore fish pump 4 remained out of service due to excessive gearbox oil leakage.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  No problems to report.  Fish ladder exits are clear of debris and the bubblers are operating satisfactorily.

STSs/VBSs:  The STS screens are in cycle run mode.  No problems were found during the October STS/VBS inspections. November inspections are tentatively scheduled to be completed on November 29.

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe:  The Juvenile Fish Bypass was placed in operation March 19 with 20 open orifices.  The power supply cord for the screen cleaner is wearing, exposing individual wires.  The screen cleaner is being operated in manual mode on a limited basis until repairs can be made.

Juvenile Bypass Facility:  The bypass was placed into operation March 19.

Juvenile Fish Sampling:  The last sample of the 2012 season occurred July 12.

Removable Spillway Weir:  Spill in support of fish passage ended September 1.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Ice Harbor Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| NA | NA | 0.0 | 0.0 | 56 | 52 | 7.3 | 7.0 |

*Unit 1 scrollcase temperature.

Other

Inline Cooling Water Strainers:  The juvenile shad out migration is plugging turbine unit cooling water strainers.  No lamprey are being found in the strainers.

Invasive Species:  No zebra mussels were observed during adult fishway inspections.

# Project:  Lower Monumental

# Biologists: Bill Spurgeon and Elizabeth Lindsey

Dates: November 16 - 22, 2012

## Turbine Operation

Units are being operated within the soft constraint 1% criteria.  Unit 3 was taken out of service for annual maintenance at 0730 hours on November 5 and remained out of service through this report period.  Unit 2 was out of service from 0655-1227 hours on November 20 for slip ring brush cleaning.

Adult Fish Passage Facility

The adult fishway was inspected by Corps biologists on November 19, 20, and 21.

Fish Ladders: Fishway exit head differentials and depths over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively) on all inspections.  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively) on all inspections.  The adult fish counting season ended on October 31.  North ladder picketed leads were raised on November 1.  South ladder picketed leads were raised on November 15.

### Fishway Entrances and Collection Channel: NSE1 and NSE 2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections.  North shore channel/tailwater head was in criteria (1’-2’) on all inspections.

SPE 1 and SPE 2 weir gates were in sill criteria (criteria: > 8’ or on sill) on all inspections.  While on sill the gate depth readings were 7.3’, 6.8’, and 7.3 feet.  South powerhouse channel/tailwater head was in criteria (1’-2’) on all inspections.

SSE1 weir gate was in depth criteria (criteria: > 8’ or on sill) on all inspections.  SSE 2 was in criteria (6’ above sill) on all inspections.  South shore channel/tailwater head was in criteria (1’-2’) this week.

Collection channel velocity was in criteria (1.5 - 4.0 ft/sec) this week.

### Auxiliary Water Supply System: AWS pumps were rotated out of service for scheduled maintenance on November 21.    AWS pump 2 was removed from service at 0940 hours on November 21 for bearing repair and shaft alignment.  Two pump operation will continue until work on pump 2 is complete, approximately April 15.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 50.7 square yards of forebay debris observed during this period.  Gatewell debris ranged from 0-35% surface coverage.  No oil was observed in other gatewells this week.

STSs/VBSs:  STS operation remains in cycle run mode.

Orifices, Collection Channel, Dewatering Structure, Flume:  The collection channel is operating with 18 orifices open.

Collection Facility:  The load and hold facility is in winter maintenance mode.

Transport Summary:  Fish transport ended October 1.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Monumental Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF)* |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 26.1 | 16.3 | 0.0 | 0.0 | 51.0 | 50.5 | 4.7 | 4.4 |

*Scrollcase temperatures.

#### Other

Inline Cooling Water Strainers:  Cooling water strainers were inspected on November 5.  No live lamprey were recovered.   Mortalities included 52 juvenile shad.

Invasive Species:  There were no zebra mussels observed at the monitoring stations on November 1.

Avian Activity:  Piscivorous bird numbers remained low this week.  Gulls, grebes, and cormorants were the prominent species observed.  Hazing ended on June 2.

Project:  Little Goose

# Biologist: George Melanson

Dates: November 16 - 22, 2012

## Turbine Operation

Turbine units 1 and 4 through 6 were available for service for most of the report period.  Unit 2 remained out of service for annual maintenance and for repair field ground errors.  Unit 3 was removed from service on November 16 for planned maintenance.  Unit 4 was forced out of service on November 16 from 0734 to 1230 hours due to a governor oil leak.  All available turbine units operated within the 1% efficiency criteria.

## Adult Fish Passage Facility

COE fisheries biologists performed measured inspections of the adult fishway on November 19, 20 and 21.

Fish Ladder: The ladder exit head differentials ranged between 0.0 and 0.1 feet (criteria < 0.5 ft.).  Water depths over the weirs held steady at 1.1 feet (criteria 1.0-1.3 ft.)  Picketed leads were removed for the season on November 6.  No debris was observed at the ladder exit.  The air bubbler used to prevent debris from collecting near the ladder exit operated satisfactorily.

Fishway Entrances and Collection Channel:  Channel to tailwater head differentials ranged between 1.4 and 1.7 feet (criteria 1.0 to 2.0 ft.). SSE weir depths ranged between 8.3 and 8.4 feet (criteria ≥8.0 ft). Depths for NPE1 ranged between 6.7 and 7.3 feet (criteria ≥7.0 ft or on sill). As a result of two pump operations and decreased channel to head differentials, NPE2 was closed on September 27. NSE weirs remain at fixed elevations of 531.5 feet and depths ranged between 7.1 and 7.6 feet (criteria ≥ 6.0 ft.).  Collection channel surface water velocities (criteria 1.5 to 4.0 fps) ranged from 1.6 to 1.7 fps near the SSE and 2.4 to 2.5 fps for inspections near the NSE.

Auxiliary Water Supply System:   Fish Pump 3 has remained out of service since September 25.  Repairs will be performed during the winter maintenance season.  Fish pumps 1 and 2 operated satisfactorily at increased RPMs (i.e.: increased speed) to provide additional “make up” water to the fish collection channel.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Up to 2,000 square feet of debris floated in front of the unit intakes.

Spillway Weir:  The weir was not operated this week.  Spill in support of fish passage ceased September 1.

ESBS/VBS:   All ESBS screens operated within criteria during this report period.  Monthly tests of ESBS screens showed all screens in working order on November 5.

Orifices, Collection Channel, Dewatering Structure, Flume:  The juvenile collection system satisfactorily operated throughout this period with 18 open orifices.

Transportation Facility:  Facility is being operated in primary by-pass mode.  All fish are being routed to the tailrace mid-channel area.  Winter maintenance work at the facility is in progress.

Transport Summary:  Fish transport ended on October 31.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Little Goose Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 25.0 | 16.7 | 0 | 0 | 50.4 | 50.0 | 5.6 | 5.2 |

*Ladder temperature.

Other

Inline Cooling Water Strainers:  All cooling water strainers were inspected on November 20.  No fish were observed.

Invasive Species:  The zebra mussel substrate monitor was inspected November 6.  No mussels were observed.  The next inspection is scheduled for December 3.

Avian Activity:   Piscivorous birds observed in the vicinity of the dam during the week included up to 66 seagulls and 12 cormorants.

Project:  Lower Granite

# Biologist(s):  Mike Halter and Ches Brooks

Dates: November 16 - 22, 2012

## Turbine Operation

Lower Granite had turbine units 1, 2, 3, 4 and 6 available for power generation during the report period.  Turbine unit 2 was taken out of service at 0704 hours on November 19 in support of annual maintenance.  The expected return to date for this unit is December 14.  Turbine unit 5 is out of service for cavitation repair.  The tentative return to service date for this unit is March 13, 2013.  All operating turbine units were run within the 1% operational criteria during this report period.

The Lower Granite forebay operating range has been increased to 735.0 – 736.0 feet as a soft constraint and 735.0 – 738.0 as a hard constraint.

## Adult Fish Passage Facility

On November 16 - 18, the Lower Granite fisheries biologists performed measured inspections of the adult fishway system.

Fish Ladder:  All criteria were met.

Fishway Entrances and Collection Channel:  Head differential readings remained within criteria at the south shore and north powerhouse fishway entrances during the weekly inspections.  The head differential readings at the north shore fishway entrances were out of criteria during all inspections with readings ranging from 0.8 to 0.9 feet (criterion 1.0’ – 2.0’).

Weir depths at the south shore fishway entrances met criteria during all weekly inspections.  The north powerhouse fishway entrances were on sill on all inspections this week due to tailwater elevations below 636.0 feet (these gates bottom out at elevations below 636.0 feet).  North powerhouse fishway entrance weir depths ranged from 7.2 to 7.5 feet.  Weir depths at the north shore entrances ranged from 4.9 to 6.9 feet on the weekly inspections.  As stated in prior reports north shore entrance 2 has been manually dogged off at 628.5 feet which is creating more weir depth than necessary at the loss of head differential.  North shore entrance 1 has not been adjusting its elevation adequately in auto mode to compensate relative to the fixed gate.  North shore weir depths are normally sacrificed in order to maintain the requisite 1.0 foot of head differential.

Velocity readings in the adult fishway collection channel transition pool area ranged from 0.95 to 1.15 feet per second and averaged 1.04 feet per second during the weekly inspections.

### Auxiliary Water Supply System:  There were no problems with the auxiliary water system during this report week.   Fish pumps 2 and 3 were operated all week.

#### Juvenile Fish Passage Facility

The juvenile fish collection system was operated in secondary bypass mode (all fish routed back to the river through the mid-river release pipe).  The system is scheduled to operate in that mode through December 15 if weather conditions permit.

Forebay Debris/Gatewell Debris/Oil:  The amount of forebay debris varied during the week due to wind strength and direction; none was removed.

ESBSs/VBSs:  VBS/ESBS video inspections last took place on October 26 and four of the screens in units 2, 4 and 6 had issues with either missing rivets or loose straps with sticks behind them.  These problems will be addressed as soon as possible.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  Juvenile fish collection gallery orifices were backflushed at regular 3 hour intervals all week.  Debris levels remained light at these points during this report period.

Transportation Facility:  The facility operated in secondary bypass mode (all fish routed back to the river through the mid-river release pipe).  This activity will continue until December 15 (weather permitting).  The separator complex is still being manned 24/7 due to fish being routed over the separator bars.  No PIT-tag detection system is available at Lower Granite unless fish are diverted through the separator.  Operation of the separator in secondary bypass mode will allow the detection of PIT-tagged juvenile fish (primarily subyearling Chinook) and help determine late season movement patterns.

Transport Summary:  All transport operations concluded on October 31.

Removable Spillway Weir:  The RSW was operated in support of general spill operations during the season.  Mandatory spill operations in support of fish passage ended on August 31.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1:  River conditions at Lower Granite Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 25.2 | 18.7 | 0.0 | 0.0 | 52.4 | 51.3 | 5.0 | 5.0 |

*Scrollcase temperature.

Other

Visual fish counting began on April 1 and continued through October 31.  Starting on November 1 until December 30, video fish counting will take place on a daily basis between the hours of 0600 – 1600.

Invasive Species:  The zebra mussel substrate near the adult fishway exit was last examined for zebra mussels on November 4.  No evidence of zebra mussels was found.  The next inspection is scheduled for early December.

Inline Cooling Water Strainers:  Cooling water strainers were last inspected for lamprey entrainment on October 29.  Zero lamprey mortalities were found in the strainers over a combined run time of 1,032.6 unit hours.  The next cooling water strainer inspections are scheduled for late November.

Research

Adult Fish Trap Operations:  Adult fish trap operations continued with a sample rate of 15%.  Scale samples will be taken from one out of every 25 hatchery steelhead.  All wild steelhead captured will be PIT-tagged and have scale and genetic samples taken.  Any previously PIT-tagged steelhead (either hatchery or wild) will have both scale and genetic samples taken for verification purposes.  The adult trap was dewatered for the winter season on November 19.

Fall Chinook Transport:  Collection of adult fall Chinook for transport to Lyons Ferry Hatchery has concluded for the season.  The last truck trip to Lyon’s Ferry took place on November 9.