U.S. ARMY CORPS OF ENGINEERS

WALLA WALLA DISTRICT

#### FISH FACILITIES WEEKLY REPORT

#39-2012

# Project:  McNary

# Biologists: Carl Dugger and Bobby Johnson

Dates: November 23 - 29, 2012

## Turbine Operation

McNary had 10 to 11 units available for power generation this week.  On November 1, the soft one percent criterion began.  At times, units ran outside the criteria at the BPA’s requests.  Unit outages are recorded in Table 1.

Table 1.  Unit Outages at McNary Dam.

| Units | Outage Dates | Outage Length | Reason |
| --- | --- | --- | --- |
| 3 | Jun 4 to Jan 12. | 7.5 months. | Rewind contract. |
| 8 | Jun 11 to Jan 12. | 7.5 months. | Rewind contract. |
| 14 | Sep 18 to Jan 30. | 4.5 months. | Turbine bearing. |
| 10 | Nov 27 to Jan 31. | 2 months. | Turbine bearing. |
| 1 & 4 to 7 | Nov 27. | 78 minutes. | ESBS camera inspection. |

## Adult Fish Passage Facilities

On November 23, 25 and 28, the McNary fisheries biologist performed measured inspections of the adult fishways.  Video counts and monitoring of adult passage is in progress.  Video counts and monitoring will continue through February 28, except when the ladders out of service for winter maintenance.

Fish Ladders:  Both ladders met all Fish Passage Plan criteria during measured inspections.  On November 24, the roving operator adjusted both Washington and Oregon ladder exit set points.  Previously, flow at the count stations has been slightly high at times.  On November 26, 28 and 29, project mechanics preformed scheduled maintenance on all Washington exit weirs.  The upper limit switch on weir 335 has not yet been replaced.  Oregon ladder exit monitoring revealed no problems and traveling screen differential measurements have been satisfactory.  However, there were multiple traveling screen alarms which the operators reset without incident.

Fishway Entrances and Collection Channel:  All Washington ladder inspection points and most Oregon ladder inspection points met criteria this week.  All week, the south powerhouse entrance weirs, SFEW1 and SFEW2, measured depths ranging from 8.2 to 8.4 feet and 8.5 to 8.7 feet, respectively.  It is possible the stilts on SFEW2 are affecting the flow out of the south entrances.  The project was able to maintain the south pool differential at 1.2 to 1.3 feet.  North powerhouse pool differentials measured between 0.8 and 0.9 feet.  On November 23 and 28, entrance weirs, NFEW2 and NFEW3, measured depths of 8.9 feet.  These north powerhouse readings are probably due to the juvenile system being in emergency bypass.  Collection channel velocities averaged 1.9 feet per second.  The new velocity meter cable remains on order.

### Auxiliary Water Supply System:  For the week, fish pumps 1 and 3 operated with blade angles of 30 degrees with no interruptions in service.  Pump 2 remains out of service for major overhaul which will require a contract.  The juvenile facility remains in emergency bypass and is no longer providing the usual 450 cfs to the north powerhouse pool.  The Wasco County PUD turbine unit had no interruptions in service this week.

#### Juvenile Fish Passage Facility

Fall bypass season continues with the system in emergency bypass due to failure of the rectangular screen cleaning device in the collection channel.  The staff continued light maintenance at the facility which has been dewatered and winterized to avoid possible freeze breakage.

Forebay Debris/Gatewell Debris/Oil:  Forebay debris was light, consisting of a mixture of wood and milfoil.  Debris distribution is mainly affected by wind direction.  The fisheries staff continued to monitor trash rack differentials and no problems were found.  No racks were cleaned.  Gatewell observations produced satisfactory results.

ESBSs/VBSs:  ESBSs are deployed in all turbine units except unit 3 which is out of service until January, 2013.  The screens in slots 1A, 1B and 7C remain in transducer bypass mode.  The ESBS in slot 1A was observed “short cycling” on November 24.  The term “short cycling” means that the cleaning brush reverses direction before reaching the top or bottom of the ESBS.  Screens in slots 1B and 7C were found doing the same on November 27 as was the screen in slot 4A during camera inspections.  In all cases, normal brush operation was restored after operators adjusted the limit set points.  Camera inspections took place on November 27 in units 1 and 4-7.  Except for the “short cycling” previously mentioned, all screens were found satisfactory.  Next week, the project will take two spare ESBSs to the yard and raise the screens associated with units 8, 10 and 14 which will be out of service past December 15.  ESBS rehabilitations continue.

The fisheries staff monitored VBS differentials, finding 2 screens out of criteria when units were operated at higher megawatt loads.  On November 26, the project cleaned these screens and 3 others.  VBS rehabilitations continued.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  This week, 42 orifices were in use and no problems were observed.  Because the ESBS rope in slot 7A is frayed, the slot’s south orifice remains closed and the north one is open.  Emergency bypass operations continued with all systems out of service.  The replacement clutch bearing for the rectangular dewatering screen cleaning device will be custom built in Japan.  The earliest possible delivery date is December 13.

Transportation Facility:  Scheduled facility maintenance continued.  All systems remain shutdown as smolt monitoring has ended for the season.  Work continued on the bypass line access walkway near the separator.  Project welders have begun rebuilding the porosity control screens.

Transport Summary:  Fish transport operations have ended for the season.

River Conditions

River conditions during the week are outlined in Table 2.  Reported data was compiled from COE websites and the control room.  The data day is from 0000 to 2400 hours.

Table 2.  River conditions at McNary Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 142.2 | 98.3 | 0.0 | 0.0 | 51.0 | 49.0 | 6.0 | 6.0 |

Other

Inline Cooling Water Strainers:  Main unit cooling water strainer examinations will occur on December 4.

Invasive Species:  Zebra mussel trap examinations will occur in late December.

Avian Activity:  Bird counts and hazing are no longer occurring.  During casual observations taken during fishway inspections, cormorants and gulls were observed in the tailrace.  Most cormorants were roosting on the navigation lock wing wall while gulls were also roosting on the wing wall or feeding in the powerhouse flow.  Mergansers were also occasionally observed.  Bird numbers appear to be fluctuating with the juvenile shad outmigration.  Emergency bypass outfall observations included gulls, cormorants and an occasional merganser.  Forebay observations included an occasional gull, a raft of gulls, groups of grebes and occasional cormorants.  Gulls were occasionally observed roosting on the rocks by the Washington shore boat dock.

The bypass outfall water cannon remained out of service.  Contractor personnel are currently repairing walkway gratings.  Pump installation will follow the walkway grating repairs.  New pump installation is expected by the third week of December.

Research:  No on site research is in progress at this time.

Project:  Ice Harbor

# Biologist:  Mark Plummer

Biological Technician:  Stephen Jeffers

Dates: November 23 - 29, 2012

## Turbine Operation

Turbine units 1, 2, 3, and 4 were available for operation this reporting period.  Turbine units 5 and 6 remain out of service.  Turbine unit 2 went out of service for annual maintenance November 26 at 0745 hours.  Turbine unit 4 was out of service for a short period November 29 to perform and complete November STSs inspections.

## Adult Fish Passage Facilities

### Fish facility personnel inspected the adult fish passage ways November 26, 27, and 28.

### Fish Ladders:  All north and south adult fish ladder inspection points (picketed leads, head differentials, fishway exits, and depth over weirs) were within criteria.  The north and south adult fish ladder picketed leads were raised November 1.

### Fishway Entrances and Collection Channel (inspection date order):  The south shore entrance (SFE) was on sill with 6.7 feet depth, on sill with 7.7 feet depth, and on sill with 7.8 feet depth. The north powerhouse entrance (NFE) was on sill with 6.7 feet depth, on sill with 7.7 feet depth, and on sill with 7.8 feet depth. The north shore entrance (NSE) was on sill with 6.9 feet depth, off sill with 7.9 feet depth, and on sill with 7.8 feet depth.  Fishway entrance criterion is 8 feet depth, greater than 8 feet depth or on sill at 332.25 per the Fish Passage Plan.  On November 26, the south Channel/tailwater differential was 2.3 feet.  Channel/tailwater differential criterion is 1 – 2 feet.  Out of criteria inspection points are reported to the shift operator for adjustments.  Channel velocities readings were 2.6 fps, 2.7 fps, and 2.2 fps.  Channel velocity criterion is 1.5 fps – 4.0 fps.

### Auxiliary Water Supply System:  Two of the 3 north shore fish pumps were operated without problems.  Six of the 8 south shore fish pumps operated without any problems.  South shore fish pump 4 remained out of service due to excessive gearbox oil leakage.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  No problems to report.  Fish ladder exits are clear of debris and the bubblers are operating satisfactorily.

STSs/VBSs:  The STS screens are in cycle-run mode.  No problems were found during the November STS/VBS inspections.  All STSs are scheduled to be removed by December 19.

Orifices, Collection Channel, Dewatering Structure, and Bypass Pipe:  The Juvenile Fish Bypass was placed into operation March 19 with 20 orifices open.  The power supply cord for the screen cleaner is wearing, exposing individual wires.  The screen cleaner was returned to full operating service November 29 at 0750 hrs.

Juvenile Bypass Facility:  The bypass was placed into operation March 19.

Juvenile Fish Sampling:  The last sample of the 2012 season occurred July 12.

Removable Spillway Weir:  Spill in support of fish passage ended September 1.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Ice Harbor Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 26.5 | 20.0 | 0.0 | 0.0 | 52 | 50 | 7.0 | 6.8 |

*Unit 1 scrollcase temperature.

Other

Inline Cooling Water Strainers:  Individual fish from the juvenile shad out migration are plugging turbine unit cooling water strainers.  No lampreys are being found in the strainers.

Invasive Species:  No zebra mussels were observed during adult fishway inspections.

# Project:  Lower Monumental

# Biologists: Bill Spurgeon and Elizabeth Lindsey

Dates: November 23 - 29, 2012

This report is pending.  Lower Monumental Weekly Report #39 will be sent separately when it becomes available.

Project:  Little Goose

# Biologist: George Melanson

Dates: November 23 - 29, 2012

## Turbine Operation

Turbine units 1, 4 and 6 were available for service for most of the report period.  Unit 2 remained out of service due to field ground errors.  Unit 3 was removed from service on November 16 for planned maintenance and exciter replacement.  Turbine unit 5 was forced out of service from November 25 through this report period due to exciter failure.  All available turbine units were operated within the soft constraint 1% efficiency criteria.

## Adult Fish Passage Facility

COE fisheries biologists performed measured inspections of the adult fishway on November 27, 28 and 29.

Fish Ladder:  The ladder exit head differentials ranged between 0.0 and 0.1 feet (criteria < 0.5 ft.).  Water depths over the weirs ranged between 1.1 and 1.2 feet (criteria 1.0-1.3 ft.)  Picketed leads were removed for the season on November 6.  No debris was observed at the ladder exit.  The air bubbler used to prevent debris from collecting near the ladder exit operated satisfactorily.

Fishway Entrances and Collection Channel:  Channel to tailwater head differentials ranged between 1.4 and 1.7 feet (criteria 1.0 to 2.0 ft.). SSE weir depths ranged between 8.2 and 8.3 feet (criteria ≥8.0 ft). Depths for NPE1 ranged between 6.7 and 7.3 feet (criteria ≥7.0 ft or on sill). As a result of 2 pump operations and decreased channel to head differentials, NPE2 was closed on September 27.  NSE weirs remain at fixed elevations of 531.5 feet and depths ranged between 7.3 and 7.7 feet (criteria ≥ 6.0 ft.).  Collection channel surface water velocities (criteria 1.5 to 4.0 fps) ranged from 1.2 to 1.5 fps near the SSE and 2.2 to 2.6 fps for inspections near the NSE.

Auxiliary Water Supply System:  Fish pump 3 has been out of service since September 25.  Repairs will be performed during the winter maintenance season.  Fish pumps 1 and 2 operated satisfactorily at increased RPMs (i.e.: increased speeds) to provide additional “make up” water to the fish collection channel.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  Up to 5,000 square feet of debris floated in front of the unit intakes.

Spillway Weir:  The weir was not operated this week.  Spill in support of fish passage ceased September 1.

ESBS/VBS:   All ESBSs operated within criteria during this report period.  Monthly manual testing of ESBSs showed all screens in working order on November 5.

Orifices, Collection Channel, Dewatering Structure, Flume:  The juvenile collection system was operated throughout this period with 18 open orifices.

Transportation Facility:  The facility is being operated in primary by-pass mode.  All fish are being routed to the tailrace mid-channel area.  Maintenance work at the facility is in progress.

Transport Summary:  Fish transport ended on October 31.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Little Goose Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 26.4 | 20.2 | 0 | 0 | 48.8 | 47.8 | 6.0 | 5.8 |

*Ladder temperature.

Other

Invasive Species:  The zebra mussel substrate monitor was inspected November 6.  No mussels were observed.  The next inspection is scheduled for December 3.

Inline Cooling Water Strainers:  All cooling water strainers were inspected on November 26.  No fish were observed.

Avian Activity:  Piscivorous birds observed in the vicinity of the dam during the week included up to 28 seagulls and 16 cormorants.

Project:  Lower Granite

# Biologist(s):  Mike Halter and Ches Brooks

Dates: November 23 - 29, 2012

## Turbine Operation

Lower Granite had turbine units 1, 3, 4 and 6 available for power generation during this report period.  Turbine unit 2 is out of service for annual maintenance.  The expected return to date for this unit is December 14.  Turbine unit 5 is out of service for cavitation repair.  The tentative return to service date for this unit is March 13, 2013.  All operating turbine units were run within the soft 1% operational criteria during this report period.

The Lower Granite forebay operating range has been increased to 735.0 – 736.0 feet as a soft constraint and 735.0 – 738.0 as a hard constraint.

## Adult Fish Passage Facility

On November 23, 25, 26 and 29 the Lower Granite fisheries biologists performed measured inspections of the adult fishway system.

Fish Ladder:  All criteria were met.

Fishway Entrances and Collection Channel:  Head differential readings remained within criteria at the south shore and north powerhouse fishway entrances during the weekly inspections.  The north shore entrances were out of criteria on the November 23, 26 and 29 inspections with head differentials of 0.9, 0.8 and 0.9 feet respectively (criterion 1.0 – 2.0 feet), but met criteria on the November 25 inspection.

Weir depths at the south shore fishway entrances met criteria during all weekly inspections.  The north powerhouse fishway entrances were on sill on the November 29 inspection due to tailwater elevations below 636.0 feet (these gates bottom out at elevations below 636.0 feet).  North powerhouse fishway entrance weir depths were 7.6 feet on this date.  North powerhouse fishway entrances met depth criteria on all other inspections this week.  Weir depths at the north shore entrances ranged from 4.9 to 6.9 feet during the weekly inspections.  North shore entrance 2 has been manually dogged off at 628.5 feet which is creating more weir depth than necessary at the loss of head differential.  North shore entrance 1 has not been adjusting its elevation adequately in auto mode to compensate relative to the fixed gate.  North shore weir depths are normally sacrificed in order to maintain the requisite 1.0 foot of head differential.

Velocity readings in the adult fishway collection channel transition pool area ranged from 0.95 to 1.15 feet per second and averaged 1.04 feet per second during the weekly inspections.

### Auxiliary Water Supply System:  There were no problems with the auxiliary water system during the report week.   Fish pumps two and three were run all week.

#### Juvenile Fish Passage Facility

The juvenile fish collection system was operated in the secondary bypass mode (all fish routed back to the river through the mid-river release pipe).  The system is scheduled to operate in that mode through December 15 if weather conditions permit.

Forebay Debris/Gatewell Debris/Oil:  The amount of forebay debris varied during the week due to wind strength and direction; none was removed.

ESBSs/VBSs:  VBS/ESBS video inspections last took place on October 26 and 4 of the screens in units 2, 4 and 6 had issues with either missing rivets or loose straps with sticks behind them.  These problems will be addressed as soon as possible.

Orifices, Collection Channel, Dewatering Structure, Bypass Pipe:  Juvenile fish collection gallery orifices were backflushed at regular 3 hour intervals all week.  Debris levels remained light at these points during this report period.

Transportation Facility:  The facility operated in secondary bypass mode (all fish routed back to the river through the mid-river release pipe).  This activity will continue until December 15 (weather permitting).  The separator complex is still being manned 24 hours per day, 7 days per week due to fish being routed over the separator bars.  No PIT-tag detection system is available at Lower Granite unless fish are diverted through the separator.  Operation of the separator in secondary bypass mode will allow the detection of PIT-tagged juvenile fish (primarily subyearling Chinook) and help determine late season movement patterns.

Transport Summary:  All transport operations concluded on October 31.

Removable Spillway Weir:  The RSW was operated in support of general spill operations during the season.  Mandatory spill operations in support of fish passage ended on August 31.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1:  River conditions at Lower Granite Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature* (oF) |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 25.8 | 21.8 | 0.0 | 0.0 | 52.7 | 48.8 | 5.0 | 4.6 |

*Scrollcase temperature.

Other

Visual fish counting began on April 1 and continued through October 31.  Since November 1, video fish counting has been taking place on a daily basis between the hours of 0600 – 1600.  Video counts are slated to continue until December 30.

Inline Cooling Water Strainers:  Cooling water strainers were inspected for lamprey on the morning of November 28.  One lamprey mortality (unit 3, north strainer) was found over a combined run time of 1,079.2 unit hours.  The next cooling water strainer inspections are scheduled for late December.

Invasive Species:  The zebra mussel substrate near the adult fishway exit was last examined for zebra mussels on November 4.  No evidence of zebra mussels was found.  The next inspection is scheduled for early December.

Research

Adult Fish Trap Operations:  Adult fish trap operations have concluded for the season.  The adult trap was dewatered and winterized on November 19.

Fall Chinook Transport:  Collection of adult fall Chinook for transport to Lyons Ferry Hatchery has concluded for the season.  The last truck trip to Lyon’s Ferry took place on November 9.