FISH FACILITIES WEEKLY REPORT

#39 - 2012

# Project:  Lower Monumental Dam

# Biologist(s):  Bill Spurgeon and Elizabeth Lindsey

Dates:  November 23- November 29, 2012

## Turbine Operation

Units are being operated in soft constraint of the 1% criteria.  Unit 3 was out of service for annual maintenance from 0730 hours on November 5 to 1236 hours on November 29.  Unit 5 was out of service from 0816 to 1402 hours on November 27 due to a failed GDACS module.  Unit 6 was out of service for 3D cam calibration from 0905 to1136 hours on November 29.

Adult Fish Passage Facility

The adult fishway was inspected by Fish Section personnel on November 27, 28, and 29.

Fish Ladders: Fishway exit head differentials and depths over the weirs were within criteria (< 0.5’ and 1.0’-1.3’, respectively) on all inspections.  Picketed lead head differentials were in criteria (< 0.4’ and < 0.3’ for north and south shore fishways, respectively) on all inspections.  The adult fish counting season ended on October 31.  North ladder picketed leads were raised on November 1.  South ladder picketed leads were raised on November 15.

### Fishway Entrances and Collection Channel:  NSE1 and NSE 2 weir gates were in depth criteria (criteria: > 8’ or on sill) on all inspections.  North shore channel/tailwater head was in criteria (1’-2’) on all inspections.

SPE 1 and SPE 2 weir gates were in sill criteria (criteria: > 8’ or on sill) on all inspections.  While on sill the gate depth readings were 7.6’, 7.2’, and 7.3 feet.  South powerhouse channel/tailwater head was in criteria (1’-2’) on all inspections.

SSE1 weir gate was in depth or sill criteria (criteria: > 8’ or on sill) on all inspections.  While on sill the gate depth reading was 7.5 feet.  SSE 2 was in criteria (6’ above sill) on all inspections.  South shore channel/tailwater head was in criteria (1’-2’) this week.

Collection channel velocity was in criteria (1.5 - 4.0 ft/sec) this week.

### Auxiliary Water Supply System: AWS pumps were rotated out of service for scheduled maintenance on November 21.  AWS pump 2 was removed from service at 0940 hours on November 21 for bearing repair and shaft alignment.  Two pump operations will continue until work on pump 2 is complete, approximately April 15.

#### Juvenile Fish Passage Facility

Forebay Debris/Gatewell Debris/Oil:  There was an average of 24.0 square yards of forebay debris observed during this period.  Gatewell debris ranged from 0-18% surface coverage.  No oil was observed in other gatewells this week.

STSs/VBSs:  STS operation remains in cycle mode.

Orifices, Collection Channel, Dewatering Structure, Flume:  The collection channel is operating with 18 orifices open.

Collection Facility:  The load and hold facility is in winter maintenance mode.

Transport Summary:  Transport ended October 1.

River Conditions

River conditions during the week are outlined in Table 1.

Table 1.  River conditions at Lower Monumental Dam.

| Daily Average River Flow (kcfs) |  | Daily Average Spill (kcfs) |  | Water Temperature (oF)* |  | Water Clarity (Secchi disk - feet) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High | Low | High | Low | High | Low | High | Low |
| 27.2 | 20.3 | 0.0 | 0.0 | 48.0 | 47.5 | 4.3 | 4.1 |

*Scrollcase temperatures.

#### Other

Inline Cooling Water Strainers:  Cooling water strainers were inspected on November 5.  No live lamprey were recovered.   Mortalities included 52 juvenile shad.

Invasive Species: There were no zebra mussels observed at the monitoring stations on November 1.

Avian Activity: Piscivorous bird numbers remained low this week.  Gulls, grebes, and cormorants were the prominent species observed.  Hazing ended on June 2.