**2017 Fish Passage Plan**

**Chapter 9 – Lower Granite Dam**

**Table of Contents**

[1. FISH PASSAGE INFORMATION 4](#_Toc493160213)

[1.1. Juvenile Fish Passage. 4](#_Toc493160214)

[1.2. Adult Fish Passage. 6](#_Toc493160215)

[2. FISH FACILITIES OPERATIONS 8](#_Toc493160216)

[2.1. General. 8](#_Toc493160217)

[2.2. Spill Management. 8](#_Toc493160218)

[2.3. Operating Criteria – Juvenile Fish Facilities. 9](#_Toc493160219)

[2.4. Operating Criteria - Adult Fish Facilities. 16](#_Toc493160220)

[2.5. Fish Facility Monitoring & Reporting. 20](#_Toc493160221)

[3. FISH FACILITIES MAINTENANCE 20](#_Toc493160222)

[3.1. Dewatering and Fish Handling. 20](#_Toc493160223)

[3.2. Maintenance - Juvenile Fish Facilities. 21](#_Toc493160224)

[3.3. Maintenance - Adult Fish Facilities. 22](#_Toc493160225)

[4. TURBINE UNIT OPERATION & MAINTENANCE 24](#_Toc493160226)

[4.1. Turbine Unit Priority Order. 24](#_Toc493160227)

[4.2. Turbine Unit Operating Range. 25](#_Toc493160228)

[4.3. Turbine Unit Maintenance. 26](#_Toc493160229)

[5. FOREBAY DEBRIS REMOVAL 32](#_Toc493160230)

[5.1. Debris Spill Coordination. 32](#_Toc493160231)


[5.2. Emergency Debris Spills. 32](#_Toc493160232)

**Lower Granite Dam**

|  |  |
| --- | --- |
| **Project Acronym\*** | LWG |
| **River Mile (RM)** | Snake River – RM 107.5 |
| **Reservoir** | Lake Lower Granite |
| **Minimum Instantaneous Flow (kcfs)** | Dec–Feb: 0 kcfs \ Mar–Nov: 11.5 kcfs |
| **Forebay Normal Operating Range (ft)** | 733’ – 738’ |
| **Tailrace Rate of Change Limit (ft/hr)** | 1.5’/hr |
| **Powerhouse Length (ft)** | 656’ |
| **Powerhouse Hydraulic Capacity (kcfs)** | 130 kcfs |
| **Turbine Units (#)** | 6 (Units 1-3 BLH Kaplan; Units 4-6 Allis Chalmers Kaplan) |
| **Turbine Unit Generating Capacity (MW)** | Rated: 810 MW (135 MW/unit) \ Maximum: 930 MW (155 MW/unit) |
| **Gatewell Orifices** | 36 orifices (2 per gatewell = 6 per unit). 35 w/10” diameter; 1 w/14” diameter (5A) |
| **Spillway Length (ft)** | 512’ |
| **Spillway Hydraulic Capacity (kcfs)** | 850 kcfs |
| **Spillbays (#)** | 8 |
| **Spillway Weirs (#)** | 1 Removable Spillway Weir (RSW) in Bay 1 |
| **Navigation Lock Length x Width (ft)** | 650’ x 84’ (Usable Space) |
| **Navigation Lock Max. Lift (ft)** | 105’ |
| **FISH STRUCTURE/OPERATION START DATE** | |
| **Transportation Research Program – NMFS \*\*** | 1975 |
| **Submersible Traveling Screens (STS)** | 1978 |
| **Extended-Length Submersible Bar Screens (ESBS)** | 1996 |
| **Juvenile Fish Transportation Program – Corps \*\*** | 1981 |
| **Removable Spillway Weir (RSW)** | 2003 |
| **Adult Fish Counts** | 1969 (North Shore); 1975 (South Shore) |

\*Project acronym designated by US Army Corps of Engineers, Northwestern Division, Columbia Basin Water Management Division. Due to the large number of projects managed by NWD, this acronym may differ from other acronyms used in the region. For example, a common acronym for Lower Granite is LGR. However, that acronym is assigned to another NWD project, thus the official Corps NWD acronym is LWG.

\*\*Smolt transportation and research done by NMFS via truck until 1978 when barges purchased. Corps began implementing transportation program in 1981.



**= Fishway Temperature Monitors (6)**

**Fishway Exit**

Figure LWG-. Lower Granite Lock & Dam General Site Plan.

Table LWG-. Lower Granite Dam Schedule of Operations and Actions Defined in the 2017 Fish Passage Plan (FPP).



1. FISH PASSAGE INFORMATION

Lower Granite Dam fish passage facilities and other structures are shown in **Figure LWG-1**. The schedule of Lower Granite Dam operations that are described in the Fish Passage Plan (FPP) and Appendices is in **Table LWG-1**.

* 1. Juvenile Fish Passage.
     1. **Juvenile Fish Facilities.** The juvenile fish facilities at Lower Granite Dam consist of a bypass system and juvenile transportation facilities. The bypass system contains extended-length submersible bar screens (ESBS) with flow vanes, improved modified balanced flow vertical barrier screens (VBS) , gatewell orifices, a bypass channel running the length of the powerhouse, and a bypass pipe to transport fish to the transportation facilities or the river. The transportation facilities include an upwell and separator structure to separate the juveniles from the excess water and adult fish, raceways for holding fish, a distribution system for distributing the fish among the raceways or to the barge or back to the river, a sampling and marking building, truck and barge loading facilities, and PIT-tag detection and diversion systems.
        1. Maintenance of juvenile fish passage facilities that may impact juvenile fish or facility operations should be conducted during winter maintenance.
     2. **Juvenile Fish Migration Timing.** Juvenile fish passage timing at Lower Granite Dam (**Table LWG-2**) is based on collection data from the most recent 10-year period and does not reflect fish guidance efficiency (FGE) or spillway passage. Salmon, steelhead, bull trout, lamprey, and other species are routinely counted.

Table LWG-. Juvenile Salmonid Passage Timing at Lower Granite Dam for Most Recent 10 Years Based on Daily & Yearly Collection Data.

|  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **Year** | **10%** | **50%** | **90%** | **# Days** | **10%** | **50%** | **90%** | **# Days** |
| **Yearling Chinook** | | | | **Subyearling Chinook** | | | |
| **2007** | 19-Apr | 4-May | 14-May | 25 | 3-Jun | 9-Jun | 12-Jul | 39 |
| **2008** | 26-Apr | 9-May | 18-May | 22 | 31-May | 20-Jun | 28-Jul | 58 |
| **2009** | 22-Apr | 7-May | 20-May | 28 | 29-May | 11-Jun | 2-Jul | 34 |
| **2010** | 24-Apr | 4-May | 21-May | 27 | 2-Jun | 9-Jun | 14-Jul | 42 |
| **2011** | 19-Apr | 8-May | 16-May | 27 | 26-May | 11-Jun | 16-Jul | 51 |
| **2012** | 14-Apr | 27-Apr | 17-May | 33 | 29-May | 13-Jun | 11-Jul | 43 |
| **2013** | 19-Apr | 8-May | 14-May | 25 | 30-May | 9-Jun | 1-Aug | 63 |
| **2014** | 19-Apr | 4-May | 17-May | 28 | 28-May | 1-Jun | 12-Jul | 45 |
| **2015** | 3-Apr | 26-Apr | 11-May | 38 | 26-May | 5-Jun | 19-Jul | 54 |
| **2016** | 13-Apr | 26-Apr | 9-May | 26 | 27-May | 10-Jun | 4-Jul | 38 |
| **10-Yr MEDIAN** | **19-Apr** | **4-May** | **16-May** | **27** | **29-May** | **9-Jun** | **13-Jul** | **44** |
| **10-Yr MIN** | **3-Apr** | **26-Apr** | **9-May** | **22** | **26-May** | **1-Jun** | **2-Jul** | **34** |
| **10-Yr MAX** | **26-Apr** | **9-May** | **21-May** | **38** | **3-Jun** | **20-Jun** | **1-Aug** | **63** |
|  | **Unclipped Steelhead** | | | | **Clipped Steelhead** | | | |
| **2007** | 1-May | 10-May | 21-May | 20 | 28-Apr | 7-May | 20-May | 22 |
| **2008** | 20-Apr | 11-May | 27-May | 37 | 28-Apr | 8-May | 21-May | 23 |
| **2009** | 22-Apr | 6-May | 29-May | 37 | 21-Apr | 1-May | 21-May | 30 |
| **2010** | 26-Apr | 19-May | 5-Jun | 40 | 25-Apr | 11-May | 4-Jun | 40 |
| **2011** | 22-Apr | 13-May | 31-May | 39 | 3-Apr | 6-May | 20-May | 47 |
| **2012** | 18-Apr | 3-May | 24-May | 36 | 16-Apr | 27-Apr | 19-May | 33 |
| **2013** | 22-Apr | 13-May | 19-May | 27 | 20-Apr | 9-May | 17-May | 27 |
| **2014** | 23-Apr | 9-May | 26-May | 33 | 21-Apr | 2-May | 22-May | 31 |
| **2015** | 16-Apr | 8-May | 24-May | 38 | 11-Apr | 27-Apr | 18-May | 37 |
| **2016** | 14-Apr | 2-May | 17-May | 33 | 15-Apr | 26-Apr | 12-May | 27 |
| **10-Yr MEDIAN** | **22-Apr** | **20-May** | **25-May** | **37** | **20-Apr** | **4-May** | **20-May** | **31** |
| **10-Yr MIN** | **14-Apr** | **2-May** | **17-May** | **20** | **3-Apr** | **26-Apr** | **12-May** | **22** |
| **10-Yr MAX** | **1-May** | **19-May** | **5-Jun** | **40** | **28-Apr** | **9-May** | **4-Jun** | **47** |
|  | **Coho** | | | | **Sockeye (Wild & Hatchery)** | | | |
| **2007** | 5-May | 15-May | 23-May | 18 | 11-May | 16-May | 21-May | 10 |
| **2008** | 6-May | 10-May | 22-May | 16 | 17-May | 20-May | 8-Jun | 22 |
| **2009** | 13-May | 21-May | 23-Jun | 41 | 21-Apr | 20-May | 28-May | 37 |
| **2010** | 6-Jun | 21-May | 5-Jul | 29 | 19-May | 30-May | 5-Jun | 17 |
| **2011** | 5-May | 15-May | 1-Jun | 27 | 4-Apr | 20-May | 4-Jun | 61 |
| **2012** | 28-Apr | 18-May | 26-May | 28 | 5-May | 19-May | 26-May | 21 |
| **2013** | 8-May | 14-May | 18-May | 10 | 15-May | 17-May | 19-May | 4 |
| **2014** | 3-May | 19-May | 26-May | 23 | 8-Apr | 3-May | 19-May | 41 |
| **2015** | 27-Apr | 13-May | 23-May | 26 | 9-May | 17-May | 20-May | 11 |
| **2016** | 26-Apr | 8-May | 15-May | 19 | 17-May | 22-May | 28-May | 11 |
| **10-Yr MEDIAN** | **5-May** | **15-May** | **24-May** | **25** | **10-May** | **19-May** | **27-May** | **19** |
| **10-Yr MIN** | **26-Apr** | **8-May** | **15-May** | **10** | **4-Apr** | **3-May** | **19-May** | **4** |
| **10-Yr MAX** | **6-Jun** | **21-May** | **5-Jul** | **41** | **19-May** | **30-May** | **8-Jun** | **61** |

* 1. Adult Fish Passage.
     1. **Adult Fish Facilities.** Adult fish passage facilities at Lower Granite Dam are made up of one south shore fish ladder with two entrances, a powerhouse collection system, north shore entrances with a transportation channel underneath the spillway to the powerhouse collection system, and an auxiliary water supply system. The powerhouse collection system is comprised of four operating floating orifices, two downstream entrances and one side entrance into the spillway basin on the north end of the powerhouse, and a common transportation channel. Four of the floating orifices and the two downstream entrances at the north end of the collection system are operated. North shore entrances are made up of two downstream entrances and a side entrance into the spillway basin with the two downstream entrances normally used. Auxiliary water is supplied from the tailrace by three electric pumps, as well as from the forebay through diffuser-14. Two pumps are normally used to provide required flows. Four weirs in the upper end of the ladder were outfitted with PIT-tag detectors in early 2003.Maintenance of adult fish facilities is scheduled for January–February to minimize impacts on upstream migrants.
     2. **Adult Fish Migration Timing & Counting.** Upstream migrants are present throughout the year and adult fish facilities are operated year-round.
        1. Adult salmon, steelhead, shad and lamprey are counted per the schedule in **Table LWG-3**, and data are posted daily at: <http://www.fpc.org/adultsalmon_home.html>. Sturgeon and bull trout are relatively infrequent and counts are reported in *Miscellaneous Fish Counts* and summarized in the *Annual Fish Passage Report*.
        2. Yearly fish counts are used to determine the earliest and latest dates of peak adult passage (**Table LWG-4**). Time-of-day (diel) distributions of adult salmonids at Lower Granite Dam fishway entrances and exits are shown in **Figure LWG-2**.

Table LWG-. Lower Granite Dam Adult Fish Counting Schedule, 3/1/2017 – 2/28/2018.

|  |  |
| --- | --- |
| **Count Period** | **Counting Method and Hours \*** |
| March 1–31 | Day Video 0400–2000 hours (PST) |
| April 1 – October 31 | Day Visual 0400–2000 hours (PST) |
| June 1 – September 30 | Night Video 2000–0400 hours (PST) |
| November 1 – December 30 | Day Video 0400–2000 hours (PST) |

\*All count hours are defined in Pacific Standard Time (PST). During Daylight Saving Time (DST), March 12 –November 5, 2017, count hours will be one hour later (DST = PST+1).

Table LWG-. Lower Granite Dam Adult Fish Count Period and Peak Passage Timing (based on yearly counts from 1975 through most recent count year).

|  |  |  |  |
| --- | --- | --- | --- |
| **Species** | **Counting Period** | **Earliest Peak** | **Latest Peak** |
| Spring Chinook | Mar 1 – Jun 17 | Apr 26 | Jun 17 |
| Summer Chinook | Jun 18 – Aug 17 | Jun 18 | Jul 17 |
| Fall Chinook | Aug 18 – Dec 30 | Sep 5 | Oct 6 |
| Steelhead | Mar 1 – Dec 30 | Sep 1 | Oct 16 |
| Sockeye | Mar 1 – Oct 31 | Jul 1 | Jul 19 |
| Lamprey | Apr 1 – Oct 31 | Jul 18 | Aug 1 |



Figure LWG-. Diel Distribution of Adult Salmonids at Lower Granite Dam Fishway Entrances and Exits (*Keefer & Caudill 2008*). [www.nwd-wc.usace.army.mil/tmt/documents/FPOM/2010/2013\_FPOM\_MEET/2013\_JUN/](http://www.nwd-wc.usace.army.mil/tmt/documents/FPOM/2010/2013_FPOM_MEET/2013_JUN/)

1. FISH FACILITIES OPERATIONS
   1. General.
      1. Research, non-routine maintenance activities, and construction will not be conducted within 100' of any fishway entrance or exit, within 50' of any other part of the adult fishway, or directly in, above, or adjacent to any fishway, unless coordinated with FPOM or FFDRWG by the Project, District Operations and/or Planning or Construction office. These distances are approximate and will be updated after data are collected and analyzed to determine the threshold for adverse impacts to adult fish behavior. Alternate actions will be considered by District and Project biologists in conjunction with the Regional fish agencies on a case-by-case basis.
      2. Currently coordinated special operations related to research are described in **Appendix A - Special Project Operations & Studies**.
      3. Emergency situations should be dealt with immediately by the Project in coordination with the Project and/or District biologist. If unavailable, the biologists will be informed immediately following the incident of steps taken to correct the situation. On a monthly basis, as necessary, the project biologist will provide FPOM a summary of any emergency actions undertaken.
      4. All activities within boat restricted zones (BRZ) will be coordinated with the Project at least two weeks in advance, unless it is deemed an emergency (see also **FPP Chapter 1 - Overview** for coordination guidance).
   2. Spill Management.
      1. Spring and summer spill operations for juvenile fish passage are defined in the *Fish Operations Plan* (FOP), included in the Fish Passage Plan as **Appendix E**.
      2. Spill at Lower Granite shall be distributed in patterns defined in **Table LWG-8, LWG-9, LWG-10**.
      3. Involuntary spill is the result of river flow above powerhouse capacity, insufficient load (lack of load), turbine unit outages (forced or scheduled), or failure of a key component of the juvenile fish passage facility which forces spill to provide juvenile fish passage.
      4. To ensure navigation safety, short-term spill adjustments may be required, including spill reduction, spill pattern adjustment, and/or spill stoppages that result in forebay exceedances of the MOP range. Actual operations will vary due to conditions such as spill patterns, turbine unit operations, experience of boat captains, etc. The Corps will make short-term spill adjustments in real-time as appropriate to provide safe navigation conditions. Additional information regarding spill-specific operations for navigation is available in the FOP (**Appendix E**).
      5. Total dissolved gas (TDG) is monitored at Lower Granite Dam as defined in **Table LWG-1**Error! Reference source not found., in accordance with the annual *TDG Monitoring Plan*, included in the *Water Management Plan* as Appendix 4 (online at: [www.nwd-wc.usace.army.mil/tmt/documents/wmp/](http://www.nwd-wc.usace.army.mil/tmt/documents/wmp/)).
   3. Operating Criteria – Juvenile Fish Facilities.
      1. **Juvenile Facilities - Winter Maintenance (December 16–March 24).**
         1. **Forebay Area and Intakes.**

Remove debris from forebay and gatewell slots.

Rake trashracks just prior to the operating season.

Measure gatewell drawdown after cleaning trashracks and with ESBSs installed.

Inspect and repair gatewell; dipnet as needed.

* + - 1. **ESBS, Flow Vanes, and VBS.**

After ESBSs are removed for winter maintenance, inspect for juvenile salmonid mortalities and all other incidental fish mortalities. Inspect ESBSs within a week after removal, or as soon as practical. All mortalities are to be counted, or otherwise estimated, for each ESBS and reported to CENWW-OD-T.

Maintenance completed on all screens.

Inspect ESBSs prior to installation and operate debris cleaner (dogged off on deck) to ensure proper operation.

Log results of trial run.

Inspect VBSs with underwater video camera at least 1x/year; repair as needed.

Inspect flow vanes to make sure they are in good condition and all surfaces smooth. Repair as needed.

ESBSs installed in at least 4 turbine units (all 6 if possible) by March 24. Remaining ESBSs installed prior to April 1.

* + - 1. **Collection Channel.**

Make-up water valves and float control equipment maintained and operational.

Orifice lights operational.

Orifices clean and valves operating correctly.

Orifice cycling and air backflush system operational.

* + - 1. **Transportation Facilities.**

42" and 72" sluice gates maintained and operating correctly.

Inclined screen clean and in good condition with no holes or damage to mesh, gaps around screen, or missing silicone.

Perforated plate smooth with no rough edges.

Wet separator and fish distribution system maintained and ready for operation.

Brushes and screens on crowders in good condition; no holes or rough edges.

Crowders maintained, tested, and operating correctly.

All valves, slide gates, and switch gates maintained and in good condition.

Retainer screens in place with no holes in screens or sharp wires protruding.

Barge and truck loading pipes should be free of debris, cracks, or blockages and barge loading boom maintained and tested.

All sampling equipment should be maintained and in good operating condition prior to watering up the facilities.

Maintain juvenile PIT-tag system as required (see *Columbia Basin PIT-tag Information System, General Gate Maintenance and Inspection, Walla Walla District*, February 2003). Coordinate with PSMFC.

Mini- and midi-tanks maintained and in good operating condition.

* + - 1. **Barges.**

All engines and pumps maintained and in good operating condition.

Fish release openings and related equipment in good operating condition.

No rough edges or support beams protruding into compartments.

No brass or galvanized fittings in circulation lines.

All loading hoses properly installed so fish will not hit sides of compartments or support beams when loading.

Loading hoses in good shape with rubber gaskets in cam lock fittings.

Inside edges of cam lock joints should be beveled to avoid sharp edges.

Warning systems tested and operational.

Provide net and/or deck covers.

Net pens maintained and installed in barge holds for transport of steelhead kelts or juveniles as required.

Deck wash systems fully operational.

Oxygen monitoring probes installed and tested; monitoring system operational.

* + - 1. **Avian Predation Areas (Forebay and Tailrace).** Inspect bird wires, water cannon, and other avian deterrent devices, and repair or replace as needed. Where possible, add additional bird wires or other deterrent devices to cover areas of known avian predation activity. Prepare avian abatement contract as needed.
      2. **Maintenance Records.** Record all maintenance and inspections.
    1. **Juvenile Fish Passage Season (March 25–December 15).** Operate March 25-October 31 for juvenile fish bypass, collection, and transport, and November 1–December 15 for adult fallbacks. Operate according to criteria below and in the *Corps of Engineers Juvenile Fish Transportation Plan* (**Appendix B**). The transportation program may be revised in accordance with the ESA Section 10 permit and NOAA Fisheries biological opinion. Project personnel shall retain authority to dewater the juvenile collection system to the extent necessary to prevent frost damage to pipes and other structures during late fall and extended winter operations.
       1. **Forebay Area and Intakes.**

Remove debris from forebay.

Inspect gatewell slots daily for debris, fish buildup, and contaminating substances (particularly oil). Clean gatewells before they become 50% covered with debris. If the volume of debris precludes the ability to keep the gatewell at least 50% clear, they should be cleaned at least once daily. If orifice flow or fish conditions are observed that indicate an orifice may be obstructed with debris, the orifice will be closed and backflushed to remove the obstruction. If the obstruction cannot be removed, the orifice will be closed and the alternate orifice for that gatewell slot operated. If both orifices become obstructed or plugged with debris the turbine unit will not be operated until the gatewell and orifices are cleared of debris.

If a visible accumulation of contaminating substances (e.g., oil) is detected in a gatewell and cannot be removed within 24 hours, the gatewell orifices shall be closed immediately and the turbine unit shut down within one hour until the material has been removed and any problems corrected. A preferred method for removing oil from the water surface is to install absorbent socks, booms, or pads capable of encapsulating the material, and tie off with a rope for later disposal. Action should be taken as soon as possible to remove oil from the gatewell so the orifice can be reopened to allow fish to exit the gatewell. Orifices shall not be closed for longer than 48 hours.

Log drawdown differentials in bulkhead slots at least once per week.

Remove debris from forebay and trashracks as necessary to maintain less than 1' of additional drawdown in gate slots (relative to drawdown with a clean screen). Additional raking may be required when heavy debris loads are present in the river or if fish condition indicates an issue.

Coordinate cleaning effort with personnel operating juvenile collection facilities.

Dip bulkhead gatewell slots to remove fish prior to installing bulkhead for dewatering bulkhead slot.

* + - 1. **ESBS, VBS, and Operating Gates.**

ESBSs and flow vanes installed in all operating turbine units by March 24.

Operate ESBSs with flow vanes attached to screen.

Operate ESBSs with debris cleaners in automatic mode. Set cleaning frequency as required to maintain clean screens and good fish condition. Change cleaning frequency as needed.

Inspect each ESBS by underwater video once per month in April, May, and June. Conduct similar inspections in August and October, focusing on at least three turbine units at the judgment of Project personnel. Spot check VBSs at the same time.

If an ESBS is damaged or fails during the juvenile fish passage season, follow procedures defined in **section 3.2.2**. In no case should a turbine unit be operated with a missing or a known non-operating or damaged ESBS, except as noted.

Up to half of the project’s ESBSs may be pulled after October 1 for maintenance as long as unscreened turbine units are not operated.

Make a formal determination at the end of season as to the adequacy of ESBS bar screen panels and debris cleaner brush, and replace components as necessary.

Measure VBS head differentials at least once per week April 1–June 30 (more frequently if required) and biweekly for the remainder of the operating season. When a head differential of 1.5' is reached, the respective turbine unit should be operated at a reduced loading (≤ 110 MW) to minimize loading on the VBS and potential fish impingement until the VBS can be cleaned. Clean VBSs as soon as possible after a 1.5' head differential is reached.

Inspect at least two VBSs in two different turbine units between spring and summer. Both units should have been operated frequently in the spring. If a debris accumulation is noted, inspect other VBSs and clean debris as necessary.

Turbine units are to be operated with raised operating gates when ESBSs are installed (March 25–December 15) to improve fish guidance efficiency (FGE), except as provided in **section 4.3**.

When extreme cold weather is forecasted to occur for an extended period of time (defined as forecasted temperatures <20oF for ≥24 hours) between Thanksgiving and December 15, ESBSs and STSs may be removed. The project will first request special permission from CENWW-OD-T. CENWW-OD-T will inform NOAA Fisheries and FPOM of the action. NOAA’s National Weather Service forecast for Lower Granite Dam is available at: <http://forecast.weather.gov/MapClick.php?lat=46.658178954000505&lon=-117.43311929599969>

* + - 1. **Collection Channel.**

Orifices clean and operating. Operate at least one orifice per gatewell slot (preferably the north orifice) unless a unit is scheduled out of service with non-operational fish screens. If the project is operating within the Minimum Operating Pool (MOP), additional orifices may be operated to maintain a full collection channel. If orifices must be closed to repair any part of the facility, do not close orifices in operating units with ESBSs in place for longer than 5 hours. If possible, keep to less than 3 hours. Reduce turbine unit loading to the lower end of the 1% range if deemed necessary by the project biologist. Monitor fish conditions in gatewells hourly or more frequently during orifice closure periods.

Orifice lights operational and operating on open orifices. Orifice lights and area lights may be turned off the evening before the channel is dewatered at the end of the season (dewatering occurs on December 16 or later) to encourage fish to exit the channel volitionally. Area lights can be turned on briefly for personnel access if necessary.

Replace all burned out orifice lights within 24 hours of notification. Orifice lights shall remain lighted 24 hours/day.

Orifice jets hitting no closer than 3’ from back wall, collection channel full.

Rotate orifices in fish screens slots weekly (6 open).

Orifice valves are either fully open or closed.

Backflush orifices in the bulkhead slots every four hours and more frequently if required. During periods of high fish and debris passage, April 1 through August 15, orifices should be inspected and backflushed more frequently as determined by the project biologist, to keep orifices clean. If debris is causing continual orifice plugging problems in a particular turbine unit gatewell, the respective turbine unit generation may be restricted to the lower end of the 1% peak turbine efficiency range to minimize orifice plugging problems.

If utilizing the automatic orifice backflush system, inspect as determined by the project biologist (but at least once per 8-hour shift unless coordinated differently) to ensure that the orifices are opening and closing correctly and are clear of debris. The project biologist will determine the frequency of automatic orifice cycling and back-flushing to maintain clear orifices.

Make-up water valves and associated float controls operational and maintaining stable channel flow.

* + - 1. **Transportation Facilities.**

42" and 72" sluice gates operational; 42” separator remote controller switch fully operational.

Maintain stable water conditions in upwell and separator. No holes, broken wires, or gaps in inclined screen. Operate separator and fish distribution system as designed.

Crowder screen brushes should be maintained in good operating condition, with no holes or sharp edges on crowder screens. Crowders should be in good operating condition.

All valves, slide gates, and switch gates in and around separator and raceways operational.

Inspect raceway and tank retainer screens to make sure they are clean with no holes or protruding wire.

Barge and truck loading pipes, hoses, and related equipment free of debris, cracks, or blockages and in good condition. Barge loading boom in good operating condition. Barge loading boom remote control system fully operational.

Inform PSMFC, in advance if possible, of situations that cause the PIT-tag system to become inoperable (e.g., power outages) or that could result in confounding the interpretation of PIT-tag data (e.g., bypassing fish from raceways to the river, operating in primary bypass mode without an operational full-flow detector, emergency dewatering).

* + - 1. **Avian Predation Areas (Forebay and Tailrace).**

Bird wires and avian deterrent devices monitored to ensure they are in good condition. Any broken wires or devices should be replaced as soon as possible.

Harassment program in place to deter avian predation in areas actively used by birds and not covered by bird wires or other devices.

Project biologists shall routinely monitor project areas to determine areas of active avian predation and, if possible, adjust harassment program to cover areas or install bird wires or other deterrent devices to discourage predation activities.

* + - 1. **Removable Spillway Weir (RSW).[[1]](#footnote-1)**

RSW in spillbay 1 will be raised and operational on the first day of spill for juvenile fish passage.

When RSW is in operation, spill through Bay 1 is fixed at approximately 6.8 kcfs. The spillgate shall be raised to where it does not touch flow passing down the RSW (at least nine stops).

When the RFC forecasts Lower Granite inflows above 200 kcfs (link below in paragraph **vi.**), coordinate with RCC and CENWW-OD-T to initiate aggressive forebay debris removal so that RSW operation will not be impeded.

Complete RSW stow (complete rotation to the landing pad) when inflow exceeds 260 kcfs, upstream river gauge flows are increasing, and forecasted inflow at Lower Granite is above 300 kcfs.

On or after June 21 (start of summer spill), when average daily total project outflow is less than 30 kcfs and forecasted to remain below 30 kcfs for 3 or more days on a declining hydrograph, the RSW will be closed and spill will be distributed in patterns with no RSW in **Table LWG-9**. The RSW will be re-opened if average daily total project outflow increases above 30 kcfs and is forecasted to remain above 30 kcfs for 3 or more days (NWRFC inflow forecast for Lower Granite at: [www.nwrfc.noaa.gov/river/station/flowplot/flowplot.cgi?LGDW1](file:///C:\Users\G0PDWLSW\Documents\Fish%20Passage%20Plans\FPP17\FPP17_Sections_Final\www.nwrfc.noaa.gov\river\station\flowplot\flowplot.cgi%3fLGDW1)).

When not spilling, operation of the RSW for short durations may be requested by the Project Biologist through CENWW during low flow years if it appears the juvenile fish transportation facility and barge holding capacities will be exceeded, as described in the *Juvenile Fish Transportation Plan* (**Appendix B**).

* + - 1. **Inspection and Record Keeping.**

Inspect fish facilities at least once every 8 hours. Inspect facilities according to fish facilities monitoring program. Record all maintenance and inspections.

* 1. Operating Criteria - Adult Fish Facilities.
     1. **Adult Facilities - Winter Maintenance (January 1 – end of February).** Maintenance will be scheduled to target returning the adult fish ladder to service by February 15 to the extent possible, and by no later than March 1.
        1. Inspect all staff gauges and water level indicators; repair and/or clean as necessary.
        2. Dewater the ladder and inspect all dewatered sections of fish facilities for projections, debris, or plugged orifices which could injure fish or impede fish passage up the ladder. The fish ladder exit trashrack must have smooth surfaces where fish pass, and must have downstream edges that are adequately rounded or padded. A spare trashrack should be on hand for use as necessary. Inspect all diffuser gratings and chambers, and the fallout fence, annually by dewatering or by using divers or video inspection techniques. All diffuser gratings and chambers are to be dewatered and physically inspected at least every 3 years. Repair deficiencies.
        3. Inspect for and clean debris from the fish ladder exit. The trashrack and picketed leads must be clean and installed correctly.
        4. Calibrate all water level measuring devices as necessary for proper facility operation.
        5. Inspect all spill gates and ensure that they are operable.
        6. Fish pumps maintained and ready for operation.
        7. Maintain adult PIT-tag system as required. Coordinate with PSMFC.
        8. Maintain the adult fish trap as required.
        9. Clean debris from the diffuser-14 trashrack (entrance). Check under the diffuser-14 ladder grating for debris accumulation and remove – if necessary. Check limit switch settings on diffuser-14 controller and ensure full operation.
     2. **Adult Fish Passage Season (March 1 – December 31).** The adult fish ladder may be returned to service as early as February 15 to the extent possible, by no later than March 1.

***Note:*** Little Goose pool may be operated within MOP (forebay elevation range 633'–634' msl), as part of the Corps' efforts to improve migration conditions for juvenile salmonids. This may result in some of the Lower Granite adult fishway entrances bottoming out on their sills prior to reaching criteria depths. Continuous operation within MOP may also result in increased pumping head on the auxiliary water supply pumps, decreasing the amount of water pumped. Fish pump #1 may be run at “slow speed” to avoid frequent tripping from an overload condition while operating within MOP.

* + - 1. **Fishway Ladder.** Water depth over weirs: 1' to 1.3'. To facilitate proper operation of adult fishway weirgate entrances, powerhouse electricians shall raise and lower individual weirgates to check the limit switch settings and make necessary adjustments and/or begin planning for necessary repairs to occur during winter maintenance (Jan 1–end of Feb). The checks must be performed while the ladder is watered up and are expected to take approximately one hour per weirgate. Checks shall be conducted near the end of the day during the period December 15-31 when adult fish passage is minimal.
      2. **Counting Window.** The crowder shall be opened to full count slot width and the picketed leads shall be removed when not counting. The crowder shall be open as far as possible to allow accurate counting and shall not be closed to less than 18” while counting. This will usually occur during high turbidity conditions to allow count accuracy criteria to be achieved. The counting slot has a width range of 12-30”. All equipment should be maintained in good condition. Counting window and backboard should be cleaned as needed to maintain good visibility.
      3. **Head on all Fishway Entrances.** Head range: 1' to 2'.
      4. **North Shore Entrances (NSE-1&2).** Elevation at top of gates on sill = 625'.

Operate both downstream gates.

Weir depth: 7' or greater below tailwater.

* + - 1. **North Powerhouse Entrances (NPE-1&2).** Elev. at top of gates on sill= 628'.

Operate both downstream gates.

Weir depth: 8' or greater below tailwater. At tailwater below elevation 636', weirs should be on sill.

* + - 1. **Floating Orifice Gates (FOGs).** Operate four FOGs (1, 4, 7, 10). Inspect fish fallout fence for debris buildup, holes, etc.
      2. **South Shore Entrances (SSE-1 & 2).**  Elevation at top of gates on sill = 625'.

Operate both gates.

Weir depth: 8' or greater below tailwater.

At tailwater below elevation 633’ weirs should be on sill.

* + - 1. **Channel Velocity.** 1.5' to 4' per second, as measured by the NPE Channel Velocity meter digital display on the Adult Fishway Biologist Snap Shot or in the panel box located in the adult fish gallery on the third floor of the powerhouse.

The channel velocity meter has a 5-minute delay to changes in flow and readings may be influenced by fish and/or debris. Readings outside of criteria should be checked after 5 minutes to verify accuracy.

* + - 1. **Tunnel Lights.** Lights in the tunnel section under the spillway shall be on during fish passage season. The mirror that is placed so that the tunnel lights can be seen should be clean and functional.
      2. **Head on Trashracks.**

Maximum head of 0.5' on ladder exit.

Maximum head on picketed leads shall be 0.3'.

Trashrack and picketed leads installed correctly.

* + - 1. **Staff Gauges and Water Level Indicators.**

All staff gauges should be readable at all water levels encountered during the fish passage season. Repair/clean as necessary.

Inform PSMFC, in advance if possible, of situations that cause the PIT-tag system to become inoperable (e.g. power outages) or that could result in confounding the interpretation of PIT-tag data (e.g. emergency dewatering).

* + - 1. **Facility Inspections.**

Powerhouse operators shall inspect adult facilities once per day shift and check computer monitor information at least once during each back shift.

Project biologists shall inspect adult facilities at least three times per week. Inspect all facilities according to fish facilities monitoring program.

Picketed leads shall be checked during all inspections to ensure they are clean and in the correct position (all the way down).

Project personnel shall check calibration of fishway control system twice per month to ensure that it is kept within calibration. This may be done as part of routine fishway inspections. Deviations in readings should be reported to the electrical crew foreman for corrective action.

Inspect fishways daily for foreign substances (particularly oil). If substances are found, corrective actions should be undertaken immediately.

Record all inspections.

* + - 1. **Adult Trap Holding Tanks.** Protocols for operating the adult trap for research and other activities are covered in **Appendix G**. This criterion supplements that appendix and governs use of the holding tanks for research or broodstock collection and water supply. The water supply for the trap comes from the diffuser water supply at the top of the ladder and trap operations can affect the amount of water in the ladder proper. Operating all six holding tanks may require that modifications be made to the auxiliary water supply to diffuser #14.

Prior to and during the period of use of any holding tanks at the Adult Trap, the COE should inspect and clean if necessary the intake to the diffuser #14 auxiliary water supply. Additionally, the COE should inspect and repair potential sources of leakage in the diffuser #14 water supply.

No holding tanks can be used prior to September 1 of each year if their usage affects the amount of water passing down the fish ladder and a water depth of less than 12 inches of water is maintained over the ladder weirs.

After September 1, the two smaller of the six holding tanks only may be used to hold adult fish for hatchery broodstock or other research needs if the use of more tanks will limit the ability of the LWG fish ladder to meet its depth over ladder weir criteria.

Additional holding tanks may be used if modifications are made to the diffuser #14 water supply that allow a water depth of 12 inches or greater over the ladder weirs in addition to meeting the needs of the additional tanks.

* + - 1. **Adult Fish Ladder Exit Pool Cooling Pumps.** Operate forebay exit pool cooling pumps that spray upstream of the fish ladder exit to enhance conditions for adult fish exiting the ladder and to supplement cooler water throughout the ladder. The water supply for the manifold at the exit pool originates from AUX pumps 1 and 2 at elevation 667’ in the forebay, which is 66’ below the MOP range (733’-734’). This action requires both pumps to be operational at the same time for optimal cooling.
         1. Begin operation of exit pool cooling pumps when the Lower Granite fish ladder exit pool water temperature is at or above 68°F. Exit pool temperature data are online at: <http://www.nwd-wc.usace.army.mil/dd/nww/fl_temps>
         2. Continue this operation until water temperature at the exit pool and the Lower Granite forebay temperature string at 0.5 meters deep are below 68°F for 3 consecutive days (forebay temperature string data are online at: <http://www.nwd-wc.usace.army.mil/ftppub/water_quality/tempstrings/>). At that time, discontinue pump operation until criteria to start pump operations are met.
         3. The pumps may be turned on or off at the Project Biologist’s discretion if adult passage delays are observed either in the forebay or within the ladder, and operation of the pumps is believed to influence the adult passage issue.
      2. **Fishway Temperature Monitoring.** From June 1 through September 30, water temperature will be monitored at adult fishway entrances and exits.

Temperature monitors shall be placed within 10 meters of all shore-oriented entrances and exits.

If possible, the entrance monitor shall be within 1 meter above the ladder floor and at least 10 meters downstream of ladder diffusers to allow for sufficient mixing with surface water.

The exit monitor shall be within 1 meter above the ladder floor and above all diffusers to allow for sufficient mixing with surface water.

If an existing temperature monitoring location is proposed to be used for either the exit or entrance, it shall be verified that the site accurately reflects water temperature within 10 meters of the entrance or exit.

Project Fisheries will submit temperature data to the Fish Passage Center (FPC) weekly for posting online at: <http://www.fpc.org/river/Q_ladderwatertempgraph.php>

* 1. Fish Facility Monitoring & Reporting.
     1. Project biologists shall inspect fish facilities at the frequencies defined in the juvenile and adult fish facilities operating criteria sections.
     2. **Weekly Reports.** Project biologists shall prepare weekly reports March 1–December 31, summarizing project operations for Friday–Thursday and email to CENWW-OD-T by noon the following Monday. Reports shall provide an overview of how the project and fish passage facilities operated during the week and evaluate resulting fish passage conditions, and include:

Any out-of-criteria situations observed and subsequent corrective actions taken;

Any equipment malfunctions, breakdowns, or damage along with a summary of resulting repair activities;

Adult fishway control calibrations;

ESBS and VBS inspections;

Any unusual activities that occurred that may have affected fish passage.

* + 1. **Annual Reports.** Project biologists shall prepare a draft annual *Adult and Juvenile Monitoring Report* by February 10 and a final report by March 15 summarizing operation of adult fish passage facilities for the previous year and giving a brief overview of the juvenile fish operations. The annual report shall also include a description of all actions taken to discourage avian predation at the project, with an overview of the effectiveness of the activities in discouraging avian predation.
    2. Project biologists also inspect project facilities once per month and during dewaterings for the presence of zebra and Quagga mussels. Biologists shall provide a report to CENWW-OD-T on a monthly basis summarizing mussel inspections.

1. FISH FACILITIES MAINTENANCE
   1. Dewatering and Fish Handling.
      1. Project biologists should be present to provide technical guidance at all project activities that may involve fish handling. All dewaterings shall be accomplished in accordance with approved *Dewatering* *Guidelines and Fish Salvage Plans* (**Appendix F**). When river temperatures reach 70°F or greater, all adult fish handling will be coordinated through CENWW-OD-T. Dewatering and fish handling plans were reviewed and revised in 2011 to ensure that they comply with **Appendix F**.
   2. Maintenance - Juvenile Fish Facilities.
      1. **Scheduled Maintenance.** Scheduled maintenance of juvenile facilities is conducted throughout the year. Long-term maintenance or modifications of facilities, which require extended out of service periods, are conducted during the winter maintenance period (December 16–March 24). During fish passage season, parts of the facilities are maintained on a daily, weekly, or longer interval to keep them in proper operating condition.
      2. **Unscheduled Maintenance.** Unscheduled maintenance is the correction of any situation that prevents facilities from operating within criteria or that will impact fish passage or survival.
         1. **Notification/Reporting**. Maintenance of facilities such as ESBSs, which sometimes break down during the fish passage season, will be carried out as described below. In these cases, repairs will be made as prescribed and CENWW-OD-T will be notified as soon as possible after it becomes apparent that repairs are required. The Operations Manager has the authority to initiate work prior to notifying CENWW-OD-T if a delay of the work will result in an unsafe situation for people, property, or fish. Unscheduled maintenance that will have a significant impact on fish passage shall be coordinated with NOAA Fisheries and FPOM on a case-by-case basis by CENWW-OD-T. Information required by CENWW-OD-T includes:

Description of the problem;

Type of outage required;

Impact on facility operation;

Length of time for repairs;

Expected impacts on fish passage and proposed measures to mitigate them.

* + - 1. **ESBSs.** The ESBSs are inspected periodically throughout the juvenile migration season with a video monitoring system. If a screen is found damaged or malfunctions at any time it will be removed and either replaced with a spare or repaired. A unit shall not be operated during the juvenile bypass season with a missing, damaged or non-operating ESBS (except as detailed below). If an ESBS fails on a weekend or at night when maintenance crews are not available, the turbine unit will be shut down and generation switched to another fully screened unit. If all screened turbine units are in service, water may be spilled until the affected ESBS can be removed and repaired or replaced.
         1. If an ESBS screen cleaner fails after 1400 hours on a regular workday or any time on a weekend, and taking the unit out of service would result in spilling above TDG state standards, the unit may be operated with the failed screen cleaner up to a maximum of 110 MWs if there is evidence that the ESBS will not plug with debris (e.g., a lack of debris in the gatewell and along the face of the powerhouse). Project personnel will pull and replace the screen the next morning, weekday or weekend inclusive. If the screen cannot be pulled and repaired the next morning, the unit will be removed from service until the screen can be repaired. If there is evidence that fish are being injured under this operation, by either observing injured fish in the gatewells or injured fish appearing on the separator, the turbine unit will be removed from service immediately. This operation will not take place when daily average river flows are less than total powerhouse capacity and the turbine unit will not be operated during power peaking operations where turbine units are being turned on and off.
      2. **Gatewell Orifices.** Each turbine intake slot has two 10" orifices with air-operated valves in the bulkhead slot for allowing the fish to exit the slots. However, turbine unit intake 5A has one 10” orifice and one 14” orifice, both with air-operated valves. Under normal operation, 18 bulkhead slot orifices (one per gatewell slot) shall be operated. Additional bulkhead slot orifices may be operated to hasten fish departure and/or allow debris to exit gatewells as the hydraulic capacity of the gallery will allow. If an orifice becomes blocked with debris it will normally be cleaned and remain in operation. If an orifice is damaged, it will be closed and the alternate orifice for that gatewell operated until repairs can be made. If both orifices are blocked with debris, damaged, or must be closed, the turbine unit will be taken out of service until repairs can be made. If repairs will take longer than 48 hours, juvenile fish will be dipped from the gatewell with a dip basket.
      3. **Bypass Pipe.** The bypass pipe goes from the end of the powerhouse bypass channel to the transportation facilities downstream. All juvenile fish in the bypass system must pass through this to the transportation facilities or to the tailrace. If any part of the bypass pipe is damaged, the gatewell orifices will be closed and the bypass system dewatered until repairs can be made. *Turbine units will not be operated for longer than 5 hours with ESBSs in place and orifices closed.*  If possible, keep to less than 3 hours. If an outage takes longer than 5 hours, spill will be provided to bypass juvenile fish. During any orifice closure, gatewells shall be monitored by project personnel for signs of fish problems or mortality. During periods of high fish passage, orifice closure times may be much less than 5 hours depending on fish numbers and condition.
      4. **Transportation Facilities.** The transportation facilities can be operated to either collect juveniles for the transportation program, and/or to bypass them back to the river. If part of the facility malfunctions or is damaged, efforts will first be made to bypass the fish around the damaged area. If this is not possible, the fish will be bypassed around the transportation facilities or the entire bypass system dewatered until repairs are made. Spill may be used as an alternative avenue for fish passage during a bypass system outage.
  1. Maintenance - Adult Fish Facilities.
     1. **Scheduled Maintenance.** Scheduled maintenance of a facility that must be dewatered or where maintenance will have a significant effect on fish passage will be done during the January–February winter maintenance period. Maintenance will be scheduled to target returning the adult ladder to service by February 15 to the extent possible, and by no later than March 1. Maintenance of facilities that will have no effect on fish passage may be conducted at any time. When facilities are not being maintained during the winter maintenance period, they will be operated according to normal criteria unless otherwise coordinated with NOAA Fisheries and other FPOM participants.
     2. **Unscheduled Maintenance.** 
        1. **Notification/Reporting.** Unscheduled maintenance of adult facilities will follow the same coordination procedures as for juvenile facilities in **section 3.2.2**. Unscheduled maintenance that will significantly affect the facility operation will be coordinated with NOAA Fisheries and FPOM. If part of a facility is damaged or malfunctions during fish passage season and the facility can still be operated within criteria with no detrimental effects on fish passage, repairs may be conducted during winter maintenance or when fewer numbers of fish are passing. If part of a facility is damaged or malfunctions and fish passage may be significantly impacted, it will be repaired as soon as possible.
        2. **Ladder and Count Station.** If any part of the ladder fails or is blocked with debris during fish passage season, efforts will first be made to correct the problem without dewatering the ladder. Trashracks, picket leads, and counting stations can sometimes be repaired or maintained without dewatering the ladder. If the fish trap malfunctions or is damaged, fish may be passed around it until repairs are made. The decision to dewater the ladder and make repairs during fish passage season or wait until the winter maintenance period will be made after coordination with the fish agencies and tribes.
           1. **Hazardous Materials Spill.** In the event of a hazardous materials spill, the Project Biologist has the authority to make fishway adjustments outside of operating criteria as necessary to prevent contamination of the ladder until unified command is formed and consultation is established with FPOM. NOAA Fisheries will be notified within 24 hours of a ladder closure.
        3. **Auxiliary Water Supply (AWS).** Three electric pumps supply auxiliary water for the fish ladder and powerhouse collection system. Two pumps are capable of providing required flows during normal operations and most flow conditions.
           1. If one pump fails during the two-pump operation, the pump on standby will be operated to make up flows.
           2. If two pumps fail and the outage is expected to be long-term, the floating orifices will be closed and monitored in the following order: OG-4, OG-7, OG-10, OG-1. If fishway criteria still cannot be met, NSE-2 and NPE-2 will be closed and NPE-1 raised in 1' increments to provide the required 1'–2' head differential. If head cannot be maintained by the time the top of the weir reaches 5', then SSE-1 and SSE-2 should be raised in 1' increments until 5' below tailwater is reached.
           3. If all three pumps fail, NSE-1 and NPE-1 should be closed, the powerhouse collection channel bulkheaded off at the junction pool, and SSE-1 and SSE-2 operated at 6' below tailwater regardless of head.
           4. If oil or other contaminants are observed in the powerhouse tailrace, the AWS pumps will be removed from service until the substance is contained and there is no risk of contamination in the ladder collection channel and transition pool. The Project Biologist will notify CENWW-OD-T as soon as possible and CENWW-OD-T will notify NOAA Fisheries and FPOM. When the problem is resolved, the Project Biologist will submit a MFR to CENWW-OD-T for distribution to FPOM (see **section 3.3.2.2.a**).
        4. **Fishway Entrances.** The fishway entrances consist of main entrance weirs with hoists and automatic controls, and floating orifices which regulate themselves with tailwater fluctuations. If any of the automatic controls malfunction, the weirs can be operated manually by project personnel and kept within criteria. If there is a further failure which prevents an entrance from being operated manually, the weirs can usually be left in a lowered position while repairs are being conducted or the entrance closed and the water redistributed to other entrances while repairs are made. If a floating orifice fails, it will be pulled out of the water and the entrance bulkheaded off until it is repaired.
        5. **Diffuser Gratings.** Diffuser chambers for adding auxiliary water to fish ladders and collection channels are covered by gratings attached by several different methods. Diffuser gratings are normally checked during the winter maintenance period to ensure they are in place. These inspections are done by either dewatering to physically inspect the diffuser gratings, or by using underwater video cameras, divers, or other methods. Diffuser gratings may come loose during the fish passage season due to a variety of reasons. Daily inspections of fish ladders and collection systems should include looking for any flow changes that may indicate problems with diffuser gratings. If a diffuser grating is known or suspected to have moved, creating an opening into a diffuser chamber, efforts must immediately be taken to correct the situation and minimize impacts on adult fish in the fishway. Coordination of problems should begin immediately through the established coordination procedure (see **section 3.2.2**). If possible, a video inspection should be made as soon as possible to determine the extent of the problem. If diffuser gratings are found to be missing or displaced, creating openings into the diffuser chambers, a method of repair shall be developed and coordinated with fish agencies and tribes through the established coordination procedure. Repairs shall be made as quickly as possible unless coordinated differently.
        6. **Fallback Fence.** The fallback fence located near the north powerhouse fishway entrances shall be inspected during winter maintenance. Loose mesh on to the frame will be reattached. If any section of the netting is severely damaged, that section will be replaced.

1. TURBINE UNIT OPERATION & MAINTENANCE
   1. Turbine Unit Priority Order.
      1. From March 1 through December 15, turbine units will be operated in the order of priority in **Table LWG-5** in order to enhance adult and juvenile fish passage. If a turbine unit is out of service for maintenance or repair, the next unit in the priority order shall be operated.
      2. Turbine unit priority order may be coordinated differently for fish research, construction, or project maintenance activities.

Table LWG-. Lower Granite Dam Turbine Unit Priority Order.

|  |  |  |
| --- | --- | --- |
| **Season** | **Duration** | **Unit Priority** |
| March 1 – December 15  Fish Passage Season | Start Units | U1 available = 1, 3, 4–6 any order, 2**a**  U1 unavailable = 2**a**, 3, 4–6 any order |
| Stop Units b | 4-6 any order, then 3, 2, 1 |
| December 16 – end of February | Stop/Start Units | Any Order |

**a.** Unit 2 has fixed Kaplan blades (non-adjustable) and operates in the upper 1% range. The priority order minimizes starts/stops and allows for the longest runtime once started. If Unit 1 is unavailable, Unit 2 will be first priority for adult attraction flow.

**b.** Stop units in reverse Start order, except Unit 2 will be stopped second to last to maintain Unit 1 for adult attraction.

* 1. Turbine Unit Operating Range.
     1. As defined in *BPA’s Load Shaping Guidelines* (**Appendix C**), turbine units will be operated within ±1% of peak turbine efficiency (1% range) from April 1–October 31, in order to minimize mortality of juvenile fish passing through turbine units. Turbine unit discharge and power output at the lower and upper limits of the 1% range for various heads are defined in **Table LWG-6** (Units 1-3), **LWG-7** (Units 4-6). If operation outside the 1% range is necessary, Project personnel shall record the information and provide to BPA on a weekly basis according to the *Guidelines*. Operation outside of 1% range may be necessary to:

Meet BPA load requirements. Load will be requested in accordance with BPA's policy, statutory requirements, and Load Shaping Guidelines (**Appendix C**);

If the draft tube is to be dewatered, the unit will be operated at full load (>1%) for a minimum of 15 minutes prior to installing tail logs. If not possible to load, the unit will be run at speed-no-load (<1%) for a minimum of 15 minutes. This is to reduce the number of fish in the unit prior to installing stop logs;

Operate a turbine unit solely to provide station service (speed-no-load); or

Comply with other coordinated fish measures.

* + 1. **Off-Season (November 1–March 31).**  While not required to do so in the off-season, turbines will normally run within the 1% range since it is the optimum point for maximizing energy output of a given unit of water over time. Operation outside the 1% range is allowed if needed for power generation or other needs.
    2. **Minimum Generation.** All of the lower Snake River powerhouses may be required to keep one generating unit online at all times to maintain power system reliability. The minimum generation range of a unit is derived from the 1% range tables below and actual unit operations, as defined in the FOP Table 1 (**Appendix E**). During low flow, there may not be enough river flow to meet this generation requirement and required minimum spill. Under these circumstances the minimum generation requirement will take precedence over the minimum spill requirement. Actual attainable minimum generation levels may vary depending on project conditions.
  1. Turbine Unit Maintenance.
     1. **Maintenance Schedule.** 
        1. Turbine unit maintenance schedules will be reviewed annually by Project and Operations Division biologists for fish impacts.
        2. Each turbine unit requires annual maintenance that may take from two to five weeks, and is normally scheduled during the mid-July to late November timeframe. Maintenance of priority units for adult passage is normally conducted in late October through December when fewer adults are migrating.
        3. Maintenance of priority units will be scheduled for winter maintenance period or when there are few fish passing the project, to the extent possible.
        4. Turbine units may occasionally require overhauls to repair major problems with the turbine or generator. Overhauls may take over one year to accomplish.
        5. Turbine units, governors, exciters, and control systems require periodic maintenance, calibration, and testing which may operation outside of the 1% range. This work will be scheduled in compliance with *BPA Load Shaping Guidelines* (**Appendix C**) to minimize impacts on juvenile fish.
     2. **Operational Testing.** Operational testing of a unit under maintenance is in addition to a unit in run status required for power plant reliability. Operational testing may deviate from FPP priority order and may require water that would otherwise be used for spill if the unit running for reliability is at its 1% lower limit (i.e., minimum generation). Water for operational testing will be used from powerhouse allocation when possible, and diverted from spill only to the extent necessary to maintain generation system reliability.
        1. Pre-Maintenance: Units may be operationally tested for up to 30 minutes before going into maintenance status by running the unit at speed-no-load and various loads within the 1% range for pre-maintenance measurements and testing, and to allow all fish to move through the unit per **section 4.3.4. Unwatering Units**.
        2. Post-Maintenance: Units may be operationally tested after maintenance or repair while remaining in maintenance or forced outage status. Operational testing may consist of running the unit for up to a cumulative time of 30 minutes (within 1% range) before it is returned to operational status.
     3. **Operating Gates.[[2]](#footnote-2)** Turbine units will be operated with operating gates in the *raised* position to improve fish passage conditions when ESBSs are installed, except as provided below:
        1. Operation of units with operating gates in the standard position shall be restricted to July 1–December 15, and shall not occur unless at least four other units are available for service. No more than one unit at a time shall be operated with operating gates in the standard operating position.
        2. The Project Biologist will be notified when the operating gates are set in standard operating position, and will monitor the gatewells twice per day to observe fish condition while operating gates are in the standard position.
        3. Operating gates are used to dewater units to facilitate annual maintenance. Unit outage periods will be minimized to the actual time required for maintenance by lowering operating gates in one unit to the standard operating position and connecting to hydraulic cylinders on the afternoon of the last regular workday (normally Thursday) prior to the start of maintenance. The unit may be operated with operating gates in the standard position until 0900 hours the next regular workday (normally Monday).
        4. After maintenance, the unit can be operated with one operating gate in the standard position until 0900 hours of the first regular workday after maintenance is completed.
        5. If unit maintenance or raising of the operating gates is delayed beyond the times stated above, the unit shall be immediately taken out of service until work can be completed.
     4. **Dewatering Units.** Dewatering turbine units should be accomplished in accordance with project dewatering plans. If the turbine unit draft tube is to be dewatered, operate unit with full load for a minimum of 15 minutes prior to installing tail logs. If not possible to load, run unit at speed-no-load for minimum of 15 minutes. This is to reduce the number of fish in the scroll case prior to installing stop logs. If a turbine unit is out of service for maintenance for an extended period of time without tailrace stop logs in place, efforts should be made to not open the wicket gates if the scroll case must be dewatered at a later date without the unit being spun beforehand.
     5. **Doble Testing.** See **Appendix A** for yearly test schedule. Transformer Doble testing is required every three years, or more frequently if there is a known problem with a transformer, and requires the associated turbine units to be out of service for 3–5 workdays. Doble testing is normally scheduled for August or early September in conjunction with other scheduled unit maintenance to minimize impacts on fish passage. To conduct testing, the transmission lines must be disconnected from the transformers and normal generation stopped. One turbine unit will operate at speed-no-load (approximately 5 kcfs) to provide project power and operation of fish passage facilities (station service). Spill may be provided to meet minimum required project discharge during testing. If Doble testing will impact priority units for fish passage, adult passage timing should be considered to minimize impacts to migrating adults. Available units will be operated in accordance with FPP priority order and within the 1% range.
        1. Lower Granite transformer T1 or T2 bank Doble testing requires daily full line outages. Unit 5 will run at speed-no-load (approximately 5 kcfs) daily to supply station service power. When T1 is tested, T2 (Units 5-6) will be returned to service at night and T1 (Units 1-4) will remain OOS for the duration of the Doble test. When T2 is tested, T1 (Units 1-4) will be returned to service at night and T2 (Units 5 and 6) will remain OOS for the duration of the Doble test. In years when Doble testing is to be performed it will normally be scheduled to begin the second full week in August from 0600-1800 hours. Details of Doble testing will be included in the Lower Granite weekly ESA report.
     6. **Turbine Unit Outages during High Flows.** During high spring flow, unit outages for inspecting fish screens, repairing research equipment (e.g., hydroacoustic or radio-telemetry), and/or other fish items may cause increased spill in order to maintain reservoir levels within operating ranges, which may result in exceeding TDG standards. It is important that this work be conducted when scheduled to ensure that facilities are working correctly and not injuring fish, and that important fish research data are collected. To facilitate this work, reservoir storage may be utilized to minimize impacts from taking turbine units out of service and increasing spill.
        1. At Lower Granite, this special operation shall take place when flow is above 120 kcfs or when increasing spill will result in TDG exceeding standards. The activities covered under these operations will be coordinated with TMT whenever possible.
        2. For scheduled inspection or repair of research equipment, reservoirs shall be drafted to MOP and allowed to fill to 1' above the MOP forebay range as work is accomplished. After the work, reservoirs will be drafted back to MOP. When inspection or repair work can be scheduled ahead of time, the following process will be followed:

Project personnel shall schedule unit outages through the approved outage scheduling procedure by noon Tuesday of the week prior to the outage.

Project personnel shall also contact CENWW-OD-T and RCC by the same time period and inform them of the intended work.

RCC will coordinate work activities through TMT, then issue a teletype with instructions to project and BPA personnel for the scheduled work.

Spill will be increased by one spillbay stop setting (about 1.7 kcfs) above passing inflow to lower the level of Lower Granite pool to MOP prior to the scheduled work taking place.

When work takes place, additional spill will not be provided and the reservoir will be allowed to refill until the reservoir is 1' above the MOP range (a 2' pondage from where the pool was when the work started). At this point, screen inspections shall stop. (At Snake River projects, this should allow about one normal workday for the scheduled work.)

At the conclusion of the work, the reservoir shall be drafted back down to MOP utilizing a one spillbay stop increase in spill above passing inflow.

If work (e.g., screen inspections) is not finished, project personnel shall schedule another turbine unit outage for a date where it can be implemented.

* + - 1. If the work is of an emergency nature that does not normally require the unit to be taken out of service (e.g., failed hydroacoustic transducer vs. failed fish screen), and cannot wait for the above process to be implemented, project personnel shall notify CENWW-OD-T and RCC for approval. If approved, the unit shall be taken out of service and the reservoir level may be operated up to 1' above the MOP range. At this point, the unit must be returned to service and the reservoir will be drafted back to the MOP range using one spillbay stop setting above passing inflows.

Table LWG-. Lower Granite Dam Turbine Units 1, 2, 3 Power (MW) and Flow (cfs) at Upper and Lower Limits of the ±1% Peak Efficiency Operating Range. a, b

|  | **Turbine Units 1b, 2, 3** | | | | | | | |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **Project Head (feet)** | **With ESBSs** | | | | **No ESBSs** | | | |
| **1% Lower Limit** | | **1% Upper Limit** | | **1% Lower Limit** | | **1% Upper Limit** | |
| **(MW)** | **(cfs)** | **(MW)** | **(cfs)** | **(MW)** | **(cfs)** | **(MW)** | **(cfs)** |
| **85** | **69.9** | **11,938** | **116.2** | **19,863** | **65.7** | **10,897** | **120.6** | **20,010** |
| 86 | 70.6 | 11,922 | 118.5 | 20,007 | 66.4 | 10,882 | 123.0 | 20,155 |
| 87 | 71.4 | 11,906 | 120.8 | 20,146 | 67.2 | 10,868 | 125.4 | 20,296 |
| 88 | 72.2 | 11,890 | 123.1 | 20,282 | 67.9 | 10,853 | 127.8 | 20,434 |
| 89 | 73.0 | 11,875 | 125.4 | 20,415 | 68.6 | 10,839 | 130.2 | 20,568 |
| **90** | **73.7** | **11,859** | **127.7** | **20,544** | **69.3** | **10,826** | **132.6** | **20,698** |
| 91 | 74.6 | 11,849 | 128.1 | 20,346 | 70.2 | 10,817 | 133.0 | 20,500 |
| 92 | 75.5 | 11,839 | 128.5 | 20,152 | 71.0 | 10,808 | 133.3 | 20,305 |
| 93 | 76.3 | 11,829 | 128.8 | 19,963 | 71.8 | 10,799 | 133.7 | 20,115 |
| 94 | 77.2 | 11,818 | 129.2 | 19,777 | 72.6 | 10,790 | 134.1 | 19,929 |
| **95** | **78.1** | **11,808** | **129.5** | **19,596** | **73.4** | **10,781** | **134.4** | **19,747** |
| 96 | 79.1 | 11,825 | 129.7 | 19,385 | 74.4 | 10,797 | 134.6 | 19,536 |
| 97 | 80.2 | 11,841 | 129.8 | 19,179 | 75.4 | 10,813 | 134.7 | 19,329 |
| 98 | 81.2 | 11,857 | 130.0 | 18,978 | 76.4 | 10,827 | 134.9 | 19,126 |
| 99 | 82.3 | 11,872 | 130.1 | 18,780 | 77.4 | 10,842 | 135.0 | 18,928 |
| **100** | **83.3** | **11,887** | **130.3** | **18,586** | **78.3** | **10,855** | **135.2** | **18,734** |
| 101 | 84.2 | 11,890 | 132.0 | 18,637 | 79.2 | 10,858 | 137.0 | 18,785 |
| 102 | 85.1 | 11,892 | 133.7 | 18,687 | 80.0 | 10,860 | 138.8 | 18,836 |
| 103 | 86.0 | 11,895 | 135.4 | 18,736 | 80.9 | 10,863 | 140.6 | 18,885 |
| 104 | 86.9 | 11,897 | 137.2 | 18,784 | 81.7 | 10,865 | 142.4 | 18,934 |
| **105** | **87.8** | **11,899** | **138.9** | **18,830** | **82.5** | **10,867** | **144.2** | **18,981** |

**a**. Tables revised to reflect new information using the 2004 Unit 3 NS index test and the 1962 model test regarding extended-length submersible bar screens.

**b**. Unit 1 restricted to operate in upper 1% range (approximately 17-19 kcfs) due to welded runner blades (non-adjustable) in 2012 to address cracks in the link pins from shear fatigue. This restriction of Unit 1 operation will continue until the unit is restored to an adjustable-blade Kaplan.

Table LWG-. Lower Granite Dam Turbine Units 4, 5, 6 Power (MW) and Flow (cfs) at Upper and Lower Limits of the ±1% Peak Efficiency Operating Range. a

|  | **Turbine Units 4, 5, 6** | | | | | | | |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **Project Head (feet)** | **With ESBSs** | | | | **No ESBSs** | | | |
| **1% Lower Limit** | | **1% Upper Limit** | | **1% Lower Limit** | | **1% Upper Limit** | |
| **(MW)** | **(cfs)** | **(MW)** | **(cfs)** | **(MW)** | **(cfs)** | **(MW)** | **(cfs)** |
| **85** | **83.9** | **13,761** | **107.2** | **17,586** | **85.1** | **13,602** | **116.0** | **18,546** |
| 86 | 85.0 | 13,769 | 108.9 | 17,652 | 86.1 | 13,600 | 117.9 | 18,616 |
| 87 | 86.1 | 13,777 | 110.7 | 17,717 | 87.2 | 13,597 | 119.8 | 18,685 |
| 88 | 87.1 | 13,784 | 112.4 | 17,780 | 88.2 | 13,595 | 121.7 | 18,751 |
| 89 | 88.2 | 13,791 | 114.2 | 17,841 | 89.2 | 13,592 | 123.5 | 18,816 |
| **90** | **89.3** | **13,798** | **115.9** | **17,900** | **90.3** | **13,589** | **125.4** | **18,879** |
| 91 | 90.3 | 13,778 | 117.1 | 17,878 | 91.4 | 13,598 | 126.8 | 18,856 |
| 92 | 91.2 | 13,759 | 118.4 | 17,857 | 92.5 | 13,607 | 128.1 | 18,834 |
| 93 | 92.1 | 13,740 | 119.6 | 17,836 | 93.7 | 13,615 | 129.4 | 18,812 |
| 94 | 93.1 | 13,722 | 120.8 | 17,815 | 94.8 | 13,623 | 130.8 | 18,791 |
| **95** | **94.0** | **13,703** | **122.0** | **17,795** | **95.9** | **13,630** | **132.1** | **18,769** |
| 96 | 95.1 | 13,707 | 122.6 | 17,676 | 96.9 | 13.620 | 132.7 | 18,645 |
| 97 | 96.1 | 13,711 | 123.1 | 17,560 | 97.9 | 13,609 | 133.3 | 18,523 |
| 98 | 97.2 | 13,714 | 123.7 | 17,446 | 98.9 | 13,599 | 133.9 | 18,403 |
| 99 | 98.3 | 13,717 | 124.2 | 17,335 | 99.9 | 13,589 | 134.5 | 18,285 |
| **100** | **99.4** | **13,720** | **124.8** | **17,225** | **100.9** | **13,579** | **135.0** | **18,170** |
| 101 | 100.4 | 13,724 | 126.0 | 17,227 | 101.9 | 13,579 | 136.4 | 18,172 |
| 102 | 101.4 | 13,728 | 127.3 | 17,229 | 102.9 | 13,580 | 137.8 | 18,174 |
| 103 | 102.5 | 13,731 | 128.6 | 17,230 | 104.0 | 13,580 | 139.1 | 18,175 |
| 104 | 103.5 | 13,735 | 129.8 | 17,232 | 105.0 | 13,581 | 140.5 | 18,177 |
| **105** | **104.5** | **13,739** | **131.1** | **17,233** | **106.0** | **13,581** | **141.9** | **18,179** |

**a**. Tables revised to reflect new information using the 2004 Unit 3 NS index test and the 1975 model test regarding extended-length submersible bar screens.

1. FOREBAY DEBRIS REMOVAL

Debris at projects can impact fish passage conditions. Debris can plug or block trashracks, VBSs, gatewell orifices, dewatering screens, separators, and facility piping resulting in fish impingement, injuries and/or descaling. Removing debris from the forebay is sometimes necessary to maintain safe and efficient fish passage conditions, navigation and other project activities. Debris can be removed from the forebay by physical removal (e.g., using boats to encircle the debris with log booms and tow it to shore where it can be removed with a crane, or using a crane and scoop from the top of the dam to remove forebay debris) or by passing the debris through the spillway with special spill and/or powerhouse operations. The preferred option is to physically remove debris when possible to avoid passing debris to the next downstream project. However, this is not always possible as some projects do not have forebay debris removal capability. In this case, the only viable alternative is to pass the debris via spill.

* 1. Debris Spill Coordination.

All special spills (other than normal spill patterns for ongoing spill operations) and project operations for passing debris will be coordinated prior to the operations taking place. Each project shall contact CENWW-OD-T at least two workdays prior to the day they want the special project operations for spilling to pass debris. Project personnel shall provide CENWW-OD-T the reason for the debris spill request including an explanation of project facilities impacted by debris, the date and time of the requested spill, and any special powerhouse or other operations required to move the debris to the spillway. Using information provided by the project, CENWW-OD-T shall coordinate the special operations with RCC, NOAA Fisheries and FPOM. When a debris spill is coordinated and approved, RCC shall issue a teletype detailing the specifics of the special operations.

* 1. Emergency Debris Spills.

Emergency spills may be implemented if necessary to pass woody debris that are accumulating in front of the spillbay weir(s), compromising the safe, unobstructed passage of fish. The operating project will immediately spill the woody debris to remove the obstructions to fish passage. The operating project will notify CENWW-OD-T of the emergency spill as soon as possible to provide notification to RCC, NOAA Fisheries and FPOM.

Table LWG-. Lower Granite Dam Spring Spill Patterns with RSW. a, b

| **LWG Spring Spill Patterns with RSW - # Gate Stops per Spillbay** | | | | | | | | **Total Stops** | **Spill** |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **Bay 1 b** | **Bay 2** | **Bay 3** | **Bay 4** | **Bay 5** | **Bay 6** | **Bay 7** | **Bay 8** | **(#)** | **(kcfs)** |
| RSW |  | 1 |  | 1 | 1 | 1 | 1 | **5** | **15.2** |
| RSW |  | 1 | 1 | 1 | 1 | 1 | 1 | **6** | **16.9** |
| RSW | 1 | 1 | 1 | 1 | 1 | 1 | 1 | **7** | **18.6** |
| RSW | 1 | 1 | 2 | 1 | 1 | 1 | 1 | **8** | **20.4** |
| RSW | 1 | 1 | 2 | 1 | 1 | 1 | 2 | **9** | **22.2** |
| RSW | 1 | 1 | 2 | 2 | 1 | 1 | 2 | **10** | **24.0** |
| RSW | 1 | 1 | 2 | 2 | 2 | 1 | 2 | **11** | **25.8** |
| RSW | 1 | 2 | 2 | 2 | 2 | 1 | 2 | **12** | **27.7** |
| RSW | 2 | 2 | 2 | 2 | 2 | 1 | 2 | **13** | **29.5** |
| RSW | 2 | 2 | 2 | 2 | 2 | 2 | 2 | **14** | **31.3** |
| RSW | 2 | 2 | 3 | 2 | 2 | 2 | 2 | **15** | **33.2** |
| RSW | 2 | 2 | 3 | 3 | 2 | 2 | 2 | **16** | **35.0** |
| RSW | 2 | 2 | 3 | 3 | 3 | 2 | 2 | **17** | **36.9** |
| RSW | 2 | 3 | 3 | 3 | 3 | 2 | 2 | **18** | **38.7** |
| RSW | 3 | 3 | 3 | 3 | 3 | 2 | 2 | **19** | **40.6** |
| RSW | 3 | 3 | 4 | 3 | 3 | 2 | 2 | **20** | **42.4** |
| RSW | 3 | 3 | 4 | 4 | 3 | 2 | 2 | **21** | **44.3** |
| RSW | 3 | 3 | 4 | 4 | 4 | 2 | 2 | **22** | **46.2** |
| RSW | 3 | 4 | 4 | 4 | 4 | 2 | 2 | **23** | **48.0** |
| RSW | 4 | 4 | 4 | 4 | 4 | 2 | 2 | **24** | **49.9** |
| RSW | 4 | 4 | 4 | 4 | 4 | 2 | 3 | **25** | **51.7** |
| RSW | 4 | 4 | 4 | 4 | 4 | 3 | 3 | **26** | **53.6** |
| RSW | 4 | 4 | 5 | 4 | 4 | 3 | 3 | **27** | **55.5** |
| RSW | 4 | 4 | 5 | 5 | 4 | 3 | 3 | **28** | **57.3** |
| RSW | 4 | 4 | 5 | 5 | 5 | 3 | 3 | **29** | **59.2** |
| RSW | 4 | 5 | 5 | 5 | 5 | 3 | 3 | **30** | **61.0** |
| RSW | 5 | 5 | 5 | 5 | 5 | 3 | 3 | **31** | **62.9** |
| RSW | 5 | 5 | 5 | 5 | 5 | 3 | 4 | **32** | **64.8** |
| RSW | 5 | 5 | 5 | 5 | 5 | 4 | 4 | **33** | **66.6** |
| RSW | 5 | 5 | 6 | 5 | 5 | 4 | 4 | **34** | **68.5** |
| RSW | 5 | 5 | 6 | 6 | 5 | 4 | 4 | **35** | **70.3** |
| RSW | 5 | 5 | 6 | 6 | 6 | 4 | 4 | **36** | **72.2** |
| RSW | 5 | 6 | 6 | 6 | 6 | 4 | 4 | **37** | **74.1** |
| RSW | 6 | 6 | 6 | 6 | 6 | 4 | 4 | **38** | **75.9** |

1. This table defines patterns in increments of one gate stop per row. Spill (kcfs) is calculated as a function of the total number of stops plus RSW spill at forebay elevation 734.0 ft.
2. RSW in Bay 1= fixed spill of ~6.8 kcfs at forebay 734.0 ft. Tainter gate does not regulate flow and should be raised ≥ 9 stops to not interfere with RSW flow. When total project outflow is < 30 kcfs, RSW will be closed and spill distributed in patterns in **Table LWG-9.**

Table LWG-. Lower Granite Dam Spill Patterns with No RSW (Bay 1 Closed). a, b

| **LWG Spill Patterns with No RSW - # Gate Stops per Spillbay** | | | | | | | | **Total Stops** | **Spill** |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **Bay 1** | **Bay 2** | **Bay 3** | **Bay 4** | **Bay 5** | **Bay 6** | **Bay 7** | **Bay 8** | **(#)** | **(kcfs)** |
| CLOSE |  |  |  |  |  |  | 1 | **1** | **1.7** |
| CLOSE | 1 |  |  |  |  |  | 1 | **2** | **3.4** |
| CLOSE | 1 |  |  | 1 |  |  | 1 | **3** | **5.1** |
| CLOSE | 1 |  |  | 1 |  | 1 | 1 | **4** | **6.8** |
| CLOSE | 1 | 1 |  | 1 |  | 1 | 1 | **5** | **8.5** |
| CLOSE | 1 | 1 |  | 1 |  | 1 | 2 | **6** | **10.3** |
| CLOSE | 2 | 1 |  | 1 |  | 1 | 2 | **7** | **12.1** |
| CLOSE | 2 | 1 |  | 1 | 1 | 1 | 2 | **8** | **13.7** |
| CLOSE | 2 | 1 | 1 | 1 | 1 | 1 | 2 | **9** | **15.4** |
| CLOSE | 2 | 1 | 1 | 2 | 1 | 1 | 2 | **10** | **17.2** |
| CLOSE | 2 | 1 | 1 | 2 | 1 | 2 | 2 | **11** | **19.0** |
| CLOSE | 2 | 2 | 1 | 2 | 1 | 2 | 2 | **12** | **20.8** |
| CLOSE | 2 | 2 | 1 | 2 | 2 | 2 | 2 | **13** | **22.6** |
| CLOSE | 2 | 2 | 2 | 2 | 2 | 2 | 2 | **14** | **24.5** |
| CLOSE | 2 | 2 | 2 | 2 | 2 | 2 | 3 | **15** | **26.4** |
| CLOSE | 2 | 2 | 2 | 2 | 2 | 3 | 3 | **16** | **28.3** |
| CLOSE | 3 | 2 | 2 | 2 | 2 | 3 | 3 | **17** | **30.2** |
| CLOSE | 3 | 3 | 2 | 2 | 2 | 3 | 3 | **18** | **32.1** |
| CLOSE | 3 | 3 | 3 | 2 | 2 | 3 | 3 | **19** | **34.0** |
| CLOSE | 3 | 3 | 3 | 2 | 3 | 3 | 3 | **20** | **35.9** |
| CLOSE | 3 | 3 | 3 | 3 | 3 | 3 | 3 | **21** | **37.8** |
| CLOSE | 3 | 3 | 3 | 3 | 3 | 3 | 4 | **22** | **39.6** |
| **CLOSE** | **3** | **3** | **3** | **3** | **3** | **4** | **4** | **23** | **41.4** |
| CLOSE | 4 | 3 | 3 | 3 | 3 | 4 | 4 | **24** | **43.2** |
| CLOSE | 4 | 4 | 3 | 3 | 3 | 4 | 4 | **25** | **45.0** |
| **CLOSE** | **4** | **4** | **4** | **3** | **3** | **4** | **4** | **26** | **46.8** |
| CLOSE | 4 | 4 | 4 | 3 | 4 | 4 | 4 | **27** | **48.6** |
| **CLOSE** | **4** | **4** | **4** | **4** | **4** | **4** | **4** | **28** | **50.4** |
| CLOSE | 4 | 4 | 4 | 4 | 4 | 4 | 5 | **29** | **52.3** |
| **CLOSE** | **5** | **4** | **4** | **4** | **4** | **4** | **5** | **30** | **54.2** |
| CLOSE | 5 | 4 | 4 | 4 | 4 | 5 | 5 | **31** | **56.1** |
| CLOSE | 5 | 5 | 4 | 4 | 4 | 5 | 5 | **32** | **58.0** |
| **CLOSE** | **5** | **5** | **5** | **4** | **4** | **5** | **5** | **33** | **59.9** |
| CLOSE | 5 | 5 | 5 | 4 | 5 | 5 | 5 | **34** | **61.8** |
| CLOSE | 5 | 5 | 5 | 5 | 5 | 5 | 5 | **35** | **63.7** |
| CLOSE | 5 | 5 | 5 | 5 | 5 | 5 | 6 | **36** | **65.6** |
| CLOSE | 5 | 5 | 5 | 5 | 5 | 6 | 6 | **37** | **67.5** |

1. This table defines patterns in increments of one gate stop per row. Spill (kcfs) is calculated as a function of the total number of stops at forebay elevation 734.0 ft (**bold** patterns evaluated w/ Corps’ LWG 1:80 physical model).
2. When total project outflow is < 30 kcfs, RSW will be closed and spill distributed in patterns in this table.

Table LWG-. [*pg 1 of 2*] Lower Granite Dam Summer Spill Patterns with RSW. a, b

| **LWG Summer Spill Patterns with RSW - # Gate Stops per Spillbay** | | | | | | | | **Total Stops** | **Spill** |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **Bay 1 b** | **Bay 2** | **Bay 3** | **Bay 4** | **Bay 5** | **Bay 6** | **Bay 7** | **Bay 8** | **(#)** | **(kcfs)** |
| RSW |  |  |  |  |  |  |  | **0** | **6.8** |
| RSW |  | 1 |  |  |  |  |  | **1** | **7.9** |
| RSW |  | 2 |  |  |  |  |  | **2** | **9.6** |
| RSW |  | 3 |  |  |  |  |  | **3** | **11.4** |
| RSW |  | 4 |  |  |  |  |  | **4** | **13.1** |
| RSW |  | 4 |  |  |  | 1 |  | **5** | **14.9** |
| RSW |  | 4 |  |  | 1 | 1 |  | **6** | **16.6** |
| RSW |  | 4 |  |  | 1 | 1 | 1 | **7** | **18.4** |
| RSW |  | 4 |  | 1 | 1 | 1 | 1 | **8** | **20.1** |
| RSW | 1 | 4 |  | 1 | 1 | 1 | 1 | **9** | **21.9** |
| RSW | 1 | 4 | 1 | 1 | 1 | 1 | 1 | **10** | **23.6** |
| RSW | 1 | 5 | 1 | 1 | 1 | 1 | 1 | **11** | **25.4** |
| RSW | 1 | 5 | 1 | 2 | 1 | 1 | 1 | **12** | **27.1** |
| RSW | 1 | 5 | 1 | 3 | 1 | 1 | 1 | **13** | **28.9** |
| RSW | 1 | 5 | 1 | 4 | 1 | 1 | 1 | **14** | **30.6** |
| RSW | 1 | 5 | 1 | 5 | 1 | 1 | 1 | **15** | **32.4** |
| RSW | 1 | 5 | 1 | 5 | 1 | 2 | 1 | **16** | **34.1** |
| RSW | 1 | 5 | 1 | 5 | 1 | 3 | 1 | **17** | **35.9** |
| RSW | 1 | 5 | 1 | 5 | 1 | 4 | 1 | **18** | **37.6** |
| RSW | 1 | 5 | 1 | 5 | 1 | 5 | 1 | **19** | **39.4** |
| RSW | 1 | 5 | 2 | 5 | 1 | 5 | 1 | **20** | **41.1** |
| RSW | 1 | 5 | 3 | 5 | 1 | 5 | 1 | **21** | **42.9** |
| RSW | 1 | 5 | 4 | 5 | 1 | 5 | 1 | **22** | **44.6** |
| RSW | 1 | 5 | 5 | 5 | 1 | 5 | 1 | **23** | **46.4** |
| RSW | 1 | 5 | 5 | 5 | 2 | 5 | 1 | **24** | **48.1** |
| RSW | 1 | 5 | 5 | 5 | 3 | 5 | 1 | **25** | **49.9** |
| RSW | 1 | 5 | 5 | 5 | 4 | 5 | 1 | **26** | **51.6** |
| RSW | 1 | 5 | 5 | 5 | 5 | 5 | 1 | **27** | **53.4** |
| RSW | 1 | 5 | 5 | 5 | 5 | 5 | 2 | **28** | **55.1** |
| RSW | 1 | 5 | 5 | 5 | 5 | 5 | 3 | **29** | **56.9** |
| RSW | 1 | 5 | 5 | 5 | 5 | 5 | 4 | **30** | **58.6** |
| RSW | 1 | 5 | 5 | 5 | 5 | 5 | 5 | **31** | **60.4** |
| RSW | 2 | 5 | 5 | 5 | 5 | 5 | 5 | **32** | **62.1** |
| RSW | 3 | 5 | 5 | 5 | 5 | 5 | 5 | **33** | **63.9** |
| RSW | 4 | 5 | 5 | 5 | 5 | 5 | 5 | **34** | **65.6** |
| RSW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | **35** | **67.4** |
| RSW | 5 | 5 | 6 | 5 | 5 | 5 | 5 | **36** | **69.1** |
| RSW | 5 | 5 | 6 | 6 | 5 | 5 | 5 | **37** | **70.9** |
| RSW | 5 | 6 | 6 | 6 | 5 | 5 | 5 | **38** | **72.6** |
| RSW | 5 | 6 | 6 | 6 | 6 | 5 | 5 | **39** | **74.4** |
| RSW | 5 | 6 | 6 | 6 | 6 | 6 | 5 | **40** | **76.1** |
| RSW | 5 | 6 | 6 | 6 | 6 | 6 | 6 | **41** | **77.9** |
| RSW | 6 | 6 | 6 | 6 | 6 | 6 | 6 | **42** | **79.6** |
| RSW | 6 | 6 | 7 | 6 | 6 | 6 | 6 | **43** | **81.4** |
| RSW | 6 | 6 | 7 | 7 | 6 | 6 | 6 | **44** | **83.1** |
| RSW | 6 | 7 | 7 | 7 | 6 | 6 | 6 | **45** | **84.9** |
| RSW | 6 | 7 | 7 | 7 | 7 | 6 | 6 | **46** | **86.6** |
| RSW | 6 | 7 | 7 | 7 | 7 | 7 | 6 | **47** | **88.4** |
| RSW | 6 | 7 | 7 | 7 | 7 | 7 | 7 | **48** | **90.1** |
| RSW | 7 | 7 | 7 | 7 | 7 | 7 | 7 | **49** | **91.9** |
| RSW | 7 | 7 | 8 | 7 | 7 | 7 | 7 | **50** | **93.6** |

1. This table defines patterns in increments of one gate stop per row. Spill (kcfs) is calculated as a function of the total number of stops plus RSW spill at forebay elevation 734.0 ft.
2. RSW in Bay 1= fixed spill of ~6.8 kcfs at forebay 734.0 ft. Tainter gate does not regulate flow and should be raised ≥ 9 stops to not interfere with RSW flow. When total project outflow is < 30 kcfs, RSW will be closed and spill distributed in patterns in **Table LWG-9.**

1. Spillway weirs provide surface passage routes via spillbay(s). Temporary, or Top, Spillway Weirs (*TSW*s) at Little Goose, McNary and John Day dams can be installed, uninstalled and moved between bays using the gantry crane. Removable Spillway Weirs (*RSW*s) at Lower Granite, Lower Monumental and Ice Harbor dams are “removed” by controlled descent to the bottom of the forebay. [↑](#footnote-ref-1)
2. Operating gates may also be referred to as “head” gates at some projects. The terms are interchangeable. [↑](#footnote-ref-2)