**DRAFT**

**2021 Fish Passage Plan**

**Chapter 4 – John Day Dam**

**Table of Contents**

[1. FISH PASSAGE INFORMATION 5](#_Toc63933640)

[1.1. Juvenile Fish Facilities and Migration Timing 5](#_Toc63933641)

[1.2. Adult Fish Facilities and Migration Timing. 7](#_Toc63933642)

[2. fish facilities Operation 9](#_Toc63933643)

[2.1. General 9](#_Toc63933644)

[2.2. Spill Management 9](#_Toc63933645)

[2.3. Operating Criteria - Juvenile Fish Facilities 10](#_Toc63933646)

[2.4. Operating Criteria - Adult Fish Facilities 15](#_Toc63933647)

[2.5. Fish Facilities Monitoring & Reporting 17](#_Toc63933648)

[3. Fish Facilities Maintenance 18](#_Toc63933649)

[3.1. Fish Facilities Routine Maintenance 18](#_Toc63933650)

[3.2. Fish Facilities Non-Routine Maintenance 20](#_Toc63933651)

[4. TURBINE UNIT OPERATION & MAINTENANCE 22](#_Toc63933652)

[4.1. Turbine Unit Priority Order 22](#_Toc63933653)

[4.2. Turbine Unit Operating Range 22](#_Toc63933654)

[4.3. Turbine Unit Maintenance 23](#_Toc63933655)

[5. Dewatering Plans 29](#_Toc63933656)

[5.1. General 29](#_Toc63933657)

[5.2. Dewatering – Adult Fish Ladders 29](#_Toc63933658)

[5.3. Dewatering – Powerhouse Fish Collection System 30](#_Toc63933659)

[5.4. Dewatering – Juvenile Bypass System (JBS) 30](#_Toc63933660)

[5.5. Dewatering – Turbine Units 30](#_Toc63933661)

[5.6. Dewatering – Navigation Lock 31](#_Toc63933662)


[6. Forebay Debris Removal 31](#_Toc63933663)

[7. Response to Hazardous Materials Spills 31](#_Toc63933664)

**John Day Dam \***


|  |  |
| --- | --- |
| **Project Acronym** | JDA |
| **River Mile (RM)** | Columbia River – RM 215.6 |
| **Reservoir** | Lake Umatilla |
| **Minimum Instantaneous Flow (kcfs)** | Dec–Feb: 12.5 kcfs \ Mar–Nov: 50 kcfs |
| **Forebay Normal Operating Range (ft)** | Nov–Jun: 260’–265’ \ Jul–Oct: 265’–268’ |
| **Tailrace Rate of Change Limit (ft)** | 3’/hr |
| **Powerhouse Length (ft)** | 1,975’ |
| **Powerhouse Hydraulic Capacity (kcfs)** | 322 kcfs |
| **Turbine Units (#)** | 16 (Units 1-16 BLH Kaplan) |
| **Turbine Generating Capacity (MW)** | Rated: 2,160 MW (135 MW/unit) \ Maximum: 2,480 MW (155 MW/unit) |
| **Gatewell Orifice Diameter (in)** | One 14” orifice per gatewell (3 per unit) = 48 total |
| **Spillway Length (ft)** | 1,228’ |
| **Spillway Hydraulic Capacity (kcfs)** | 2,250 kcfs |
| **Spillbays (#)** | 20 |
| **Spillway Weirs (#)** | 2 Temporary Spillway Weirs (TSW) Bays 18, 19 |
| **Navigation Lock Length x Width (ft)** | 650’ x 86’ |
| **Navigation Lock Max. Lift (ft)** | 113’ |

\* More information is available on the Corps Portland District website for John Day Dam at: [www.nwp.usace.army.mil/Locations/Columbia-River/John-Day/](http://www.nwp.usace.army.mil/Locations/Columbia-River/John-Day/)



**Ladder Temperature Monitors**

Figure JDA-1. John Day Dam South Fish Ladder, Powerhouse Collection System, and Juvenile Bypass System.



**Ladder Temperature Monitors**

Figure JDA-2. John Day Dam Spillway and North Fish Ladder.

Table JDA-1. John Day Dam Schedule of Operations and Actions Defined in the 2020 Fish Passage Plan.



1. FISH PASSAGE INFORMATION

Fish passage facilities at John Day Lock & Dam are shown in **Figures JDA-1** and **JDA-2**. The annual schedule of project operations, maintenance, and other actions that are described in the Fish Passage Plan (FPP) and Appendices is in **Table JDA-1**.

* 1. Juvenile Fish Facilities and Migration Timing
     1. **Juvenile Facilities**. The Juvenile Bypass System (JBS) at John Day Dam was completed in 1987 and the Smolt Monitoring Facility (SMF) was completed in 1998. Maintenance of juvenile fish facilities is scheduled from approximately December 16 through March 31 to minimize impact on downstream migrants and reduce the possibility of adult fallbacks through turbine units. During this time, the JBS will be dewatered.
     2. Each of the project’s 16 turbine units include one vertical barrier screen (VBS), one submersible traveling screen (STS), and three 14"-diameter orifices (one per gatewell).
     3. During SMF juvenile fish sampling, flow with collected fish from the SMF is sent over the crest gate and down an elevated chute to the dewatering structure that reduces flow to 30 cubic feet per second (cfs) before entering the transport flume. A switch gate diverts fish to either the SMF or directly to the outfall (emergency bypass only). Fish diverted for sampling pass a fish/debris separator that directs debris and adult fish into a separate flume to the outfall. Juvenile fish are interrogated by PIT-tag detectors and diverted either to the SMF for sampling or the outfall. When the SMF is not in operation, the bypass collection conduit connects to a transport channel that carries fish to the tailrace (bypass mode). The differential between the forebay and bypass conduit is controlled by the tainter gate.
     4. **Juvenile Migration Timing & Counting**. Juvenile salmonid passage timing at John Day Dam has been determined by gatewell and SMF sampling (**Table JDA-2**). Sample collection will continue through September 15 and PIT-tag interrogation will continue through November 30 (weather permitting). The JBS will operate through December 15. Bull trout, lamprey, juvenile sturgeon, and non-listed fish are recorded as by-catch in the SMF report.
     5. Results to-date of ongoing research show significant daytime passage during daytime operations. Juvenile fish passage increases dramatically at dusk and peaks around 2300–2400 hours with a long period of elevated passage until dawn when passage decreases. Gatewell sampling data[[1]](#footnote-1) indicate that roughly 80% of juvenile migrants pass John Day Dam between 2100 and 0600 hours. During the peak spring juvenile migration period at John Day Dam, 40% of spring Chinook and steelhead passage occurred between 0700 and 2200 hours.

Table JDA-2. Juvenile Salmonid Passage Timing at John Day Dam for Most Recent 10 Years (based on daily & yearly collection data).\*

|  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **Year** | **10%** | **50%** | **90%** | **# Days** | **10%** | **50%** | **90%** | **# Days** |
| **Yearling Chinook** | | | | **Subyearling Chinook** | | | |
| **2011** | 2-May | 17-May | 28-May | 27 | 16-Jun | 14-Jul | 3-Aug | 49 |
| **2012** | 27-Apr | 6-May | 22-May | 26 | 27-Jun | 13-Jul | 29-Jul | 33 |
| **2013** | 27-Apr | 12-May | 24-May | 28 | 20-Jun | 3-Jul | 15-Jul | 26 |
| **2014** | 28-Apr | 9-May | 24-May | 27 | 21-Jun | 5-Jul | 20-Jul | 30 |
| **2015** | 20-Apr | 13-May | 24-May | 35 | 10-Jun | 23-Jun | 30-Jun | 21 |
| **2016** | 18-Apr | 30-Apr | 10-May | 23 | 13-Jun | 29-Jun | 7-Jul | 25 |
| **2017** | 24-Apr | 8-May | 18-May | 25 | 9-Jun | 1-Jul | 15-Jul | 37 |
| **2018 (March 1 start)** | 20-Apr | 8-May | 20-May | 31 | 4-Jun | 29-Jun | 19-Jul | 46 |
| **2019 (March 1 start)** | 19-Apr | 7-May | 23-May | 35 | 8-Jun | 30-Jun | 16-Jul | 39 |
| **2020** | 26-Apr | 12-May | 24-May | 29 | 7-Jun | 27-Jun | 22-Jul | 46 |
| **MEDIAN\*** | **28-Apr** | **14-May** | **29-May** | **32** | **16-Jun\*\*** | **29-Jun\*\*** | **28-Jul\*\*** | **43\*\*** |
| **MIN\*** | **20-Apr** | **6-May** | **22-May** | **24** | **6-Jun\*\*** | **27-Jun\*\*** | **20-Jul\*\*** | **31\*\*** |
| **MAX\*** | **6-May** | **27-May** | **20-Jun** | **46** | **27-Jun\*\*** | **30-Jul\*\*** | **22-Aug\*\*** | **59\*\*** |
|  | **Unclipped Steelhead** | | | | **Clipped Steelhead** | | | |
| **2011** | 25-Apr | 19-May | 31-May | 37 | 19-Apr | 19-May | 30-May | 42 |
| **2012** | 25-Apr | 1-May | 19-May | 25 | 25-Apr | 3-May | 15-May | 21 |
| **2013** | 21-Apr | 13-May | 27-May | 37 | 29-Apr | 8-May | 21-May | 23 |
| **2014** | 23-Apr | 9-May | 27-May | 35 | 30-Apr | 8-May | 21-May | 22 |
| **2015** | 16-Apr | 18-May | 28-May | 43 | 28-Apr | 14-May | 28-May | 31 |
| **2016** | 18-Apr | 28-Apr | 12-May | 25 | 22-Apr | 30-Apr | 10-May | 19 |
| **2017** | 24-Apr | 6-May | 28-May | 35 | 24-Apr | 4-May | 22-May | 29 |
| **2018 (March 1 start)** | 22-Apr | 8-May | 30-May | 39 | 20-Apr | 2-May | 22-May | 33 |
| **2019 (March 1 start)** | 21-Apr | 27-Apr | 21-May | 31 | 19-Apr | 25-Apr | 11-May | 23 |
| **2020** | 4-May | 25-May | 30-May | 27 | 2-May | 12-May | 28-May | 27 |
| **MEDIAN\*** | **26-Apr** | **13-May** | **29-May** | **34** | **29-Apr** | **14-May** | **29-May** | **31** |
| **MIN\*** | **16-Apr** | **1-May** | **19-May** | **24** | **15-Apr** | **2-May** | **15-May** | **21** |
| **MAX\*** | **6-May** | **28-May** | **8-Jun** | **51** | **7-May** | **29-May** | **10-Jun** | **44** |
|  | **Coho** | | | | **Sockeye (Wild & Hatchery)** | | | |
| **2011** | 10-May | 23-May | 6-Jun | 28 | 10-May | 22-May | 2-Jun | 24 |
| **2012** | 6-May | 21-May | 5-Jun | 31 | 2-May | 11-May | 25-May | 24 |
| **2013** | 6-May | 19-May | 1-Jun | 27 | 10-May | 19-May | 28-May | 19 |
| **2014** | 3-May | 17-May | 31-May | 29 | 14-May | 22-May | 31-May | 18 |
| **2015** | 23-Apr | 20-May | 4-Jun | 43 | 11-May | 20-May | 27-May | 17 |
| **2016** | 26-Apr | 8-May | 24-May | 29 | 30-Apr | 10-May | 22-May | 23 |
| **2017** | 2-May | 18-May | 1-Jun | 31 | 30-Apr | 14-May | 24-May | 25 |
| **2018 (March 1 start)** | 6-May | 20-May | 2-Jun | 28 | 6-May | 12-May | 26-May | 21 |
| **2019 (March 1 start)** | 27-Apr | 17-May | 6-Jun | 41 | 5-May | 19-May | 31-May | 27 |
| **2020** | 26-Apr | 4-May | 30-May | 35 | 10-May | 20-May | 30-May | 21 |
| **MEDIAN\*** | **8-May** | **22-May** | **5-Jun** | **30** | **10-May** | **21-May** | **2-Jun** | **24** |
| **MIN\*** | **23-Apr** | **13-May** | **31-May** | **24** | **30-Apr** | **11-May** | **25-May** | **16** |
| **MAX\*** | **17-May** | **3-Jun** | **14-Aug** | **90** | **1-Jun** | **14-Jun** | **27-Jun** | **41** |

\* **MEDIAN, MIN, MAX** for spring migrants based on 1998-2015 data only; data from 2016-present excluded due to potential bias from every-other-day sampling and March sampling in 2018 and 2019.

\*\* Subyearling Chinook based on 1998-2005 data only; data from 2006-present excluded due to potential bias from missed sample days during high water temperature sampling protocols (per **Appendix K**).

* 1. Adult Fish Facilities and Migration Timing.
     1. **Adult Fish Passage Facilities**. The John Day Dam adult fish facilities include a north shore ladder to pass fish from entrances at the north end of the spillway, and a south shore ladder to pass fish from entrances along a collection channel extending the full length of the powerhouse. Auxiliary water is pumped from the tailrace to all collection systems. South auxiliary water also includes forebay water from the fish turbines. Counting stations are provided in both fishways. Annual maintenance of adult fish facilities is scheduled December 1 through the end of February (winter maintenance period) to minimize impacts on upstream migrants.
     2. **Adult Fish Migration Timing & Counting**.
        1. Upstream migrants are present throughout the year and adult passage facilities are operated year-round. Counting of adult salmon, steelhead, bull trout, lamprey, and shad occurs during the dates defined for the current year in **Table JDA-3** and daily counts are posted online.[[2]](#footnote-2) The presence of other species (i.e., sturgeon, grass carp, Atlantic salmon, etc.) are recorded as comments and reported in the *Annual Fish Passage Report*.
        2. Yearly counts through the most recent passage year are used to determine the earliest and latest dates of peak adult fish passage defined in **Table JDA-4**.
        3. Time-of-day (diel) distributions of adult salmonid activity at John Day Dam fishway entrances and exits are shown in **Figure JDA-2**.

Table JDA-3. John Day Dam Adult Fish Count Schedule in 2021.

|  |  |
| --- | --- |
| **Count Period** | **Counting Method and Hours\*** |
| April 1 – October 31 | Day Visual 0500–2100 hours (PDT) |
| June 15 – September 30 | Night Video 2100–0500 hours (PDT) |

\*PST = Pacific Standard Time; PDT = Pacific Daylight Time, in effect during daylight saving time 3/14/21–11/7/21.

Table JDA-4. John Day Dam Adult Count Period and Peak Passage Timing (based on yearly counts since 1968, except lamprey since 2000).

|  |  |  |  |
| --- | --- | --- | --- |
| **Species** | **Count Period** | **Earliest Peak** | **Latest Peak** |
| Spring Chinook | Apr 1 – Jun 5 | Apr 14 | May 24 |
| Summer Chinook | Jun 6 – Aug 5 | Jun 7 | Aug 2 |
| Fall Chinook | Aug 6 – Oct 31 | Sep 2 | Sep 25 |
| Steelhead | Apr 1 – Oct 31 | Aug 25 | Oct 6 |
| Sockeye | Apr 1 – Oct 31 | Jun 21 | Jul 10 |
| Coho | Apr 1 – Oct 31 | Sep 4 | Oct 26 |
| Lamprey | Apr 1 – Oct 31 | Jun 30 | Aug 12 |



Figure JDA-3. Diel Distribution of Adult Salmonids at John Day Dam Fishway Entrances and Exits (*Keefer & Caudill 2008 – report and summary letter available online at:* [pweb.crohms.org/tmt/documents/FPOM/2010/2013\_FPOM\_MEET/2013\_JUN/](http://pweb.crohms.org/tmt/documents/FPOM/2010/2013_FPOM_MEET/2013_JUN/))

1. fish facilities Operation
   1. General
      1. Research, non-routine maintenance, fish-related activities, and construction will not be conducted within 100' of any fishway entrance or exit, within 50' of any other part of the adult fishway, or directly in, above, or adjacent to any fishway, unless coordinated with FPOM or FFDRWG by the Project, District Operations and/or Planning or Construction office. Alternate actions will be considered by District and Project biologists in conjunction with the Regional fish agencies on a case-by-case basis.
      2. Yearly special operations related to research are described as currently coordinated in **Appendix A - Special Project Operations & Studies**.
      3. Emergency situations should be dealt with immediately by the Project in coordination with the Project and/or District biologist. If unavailable, the biologists will be informed immediately following the incident of steps taken to correct the situation. On a monthly basis, as necessary, the Project Biologist will provide FPOM a summary of any emergency actions undertaken.
      4. All activities within boat restricted zones (BRZ) will be coordinated with the Project at least two weeks in advance, unless deemed an emergency (see **Chapter 1 - Overview**).
   2. Spill Management
      1. Spring and summer spill operations for juvenile fish passage are defined in the *Fish Operations Plan* (FOP), included in the Fish Passage Plan as **Appendix E**. Spill patterns formulated with spillway deflectors in place for both adult and juvenile passage are defined in **Tables JDA-8,** **JDA-9**. Spill pattern modifications for barge traffic entering the navigation lock have been coordinated with the fish agencies and tribes through the proper regional fish forums (e.g., TMT, FPOM, FFDRWG). Minimum spill is 30% April 10–August 31 to provide adequate conditions in the tailrace for juvenile egress.
      2. Excessive total dissolved gas (TDG) may harm fish and will be controlled to the extent possible, subject to river conditions. Management tools include system-wide spill distribution through the Spill Priority List issued by the Corps Northwestern Division Reservoir Control Center (RCC), night and/or day spill limits, and shaping of spill. Monitoring of TDG at John Day Dam occurs during the periods defined in **Table JDA-1**, pursuant to the Corps’ annual *TDG Management Plan* and the current *Dissolved Gas Monitoring Plan of Action*.[[3]](#footnote-3)
      3. From August 15 through November 30, adult fish attraction flow will be provided by spilling through Bay 2 open one stop (approximately 1.6 kcfs) during daylight hours defined in **Table JDA-5**.

Table JDA-5. Daytime Spill Hours for Adult Attraction at John Day Dam, Sep 1–Nov 30.

|  |  |  |
| --- | --- | --- |
| **Date**  **Range** | **Daytime Spill Hours** | |
| **Begin** | **End** |
| January 1–19 | 0700 | 1730 |
| January 20 – February 14 | 0630 | 1800 |
| February 15 – March 1 | 0600 | 1830 |
| March 2 – Start DST a | 0600 | 1930 |
| Start DST a – Apr 2 | 0700 | 2030 |
| April 3–20 | 0600 | 2130 |
| April 21 – May 16 | 0600 | 2200 |
| May 17 – June 30 | 0530 | 2230 |
| July 1–31 | 0530 | 2300 |
| August 1–15 | 0600 | 2245 |
| August 16–31 | 0600 | 2130 |
| September 1–16 | 0630 | 2100 |
| September 17 – October 4 | 0700 | 2030 |
| October 5–19 | 0730 | 2000 |
| October 20–29 | 0730 | 1930 |
| October 30 – End DST a | 0730 | 1800 |
| End DST a – December 31 | 0630 | 1700 |

**a.** DST = Daylight Saving Time, in effect from the second Sunday in March through the first Sunday in November.

* 1. Operating Criteria - Juvenile Fish Facilities
     1. **Juvenile Fish Facilities - Winter Maintenance Period (December 1 – March 31)**
        1. From December 1 through December 15, submersible traveling screens (STS) will remain in place and the juvenile bypass system (JBS) channel will operate for adult fallbacks, thereby shortening some aspects of the winter maintenance period by two weeks. During this period, priority units will be screened to the extent practicable (barring operational failure). STSs will only be removed from non-priority units when necessary to begin maintenance. After December 15, all STSs may be removed.
        2. All units are available to meet power demands.
        3. Remove debris from the forebay, all trash racks, and gatewell slots so these areas are debris-free by April 1.
        4. Inspect all VBSs for damage, holes, debris accumulations, or protrusions (video inspection is acceptable). Clean and repair when necessary.
        5. Inspect and operate each STS. Install STSs in each intake slot of all operational units by April 1, unless otherwise coordinated with the fish agencies and tribes.
        6. Inspect all gatewell orifices and orifice lighting systems. Clean and/or repair where necessary such that these systems are debris-free and operable on April 1.
        7. Check automatic control calibration/operation for the DSM tainter gate and other necessary sensors weekly. Recalibrate as necessary and report summaries of equipment recalibration in the weekly SMF operation monitoring reports.
        8. Dewater the downstream migrant (DSM) channel only when required for inspection, maintenance, or structural modifications (see **section 5**). Minimize the outage duration to the extent practicable.
        9. Inspect and maintain DSM conduit tainter gate. Repair where necessary.
        10. Inspect walls and floor of DSM conduit, raceway, and outfall. Correct any deficiencies.
        11. Inspect spillbay gates and associated control system. Repair where necessary. Spillbays must be able to achieve FPP spill patterns on April 10, unless otherwise coordinated.
        12. At the SMF, ensure all of the following items are fully operational:

Dewatering facilities, including weir gates, perforated plates, screens (free of holes or gaps), and screen cleaner brush system;

All valves and auxiliary water systems;

Flushing water valves and their perforated plates;

All gates, including the crest, tainter, switch, and rotating gates;

Fish/debris separator, including perforated plates and adult passage chamber;

PIT-tag detectors;

All sampling building systems, including holding tanks, valves, and conduits (see specific list in the *SMF Operation & Maintenance Manual*).

* + - 1. Avian abatement measures shall be in place by April 1 or as soon as weather permits. For more information, see the *Predation Monitoring & Deterrence Action Plans* for John Day Dam in **Appendix L**, Table 1 and section 4.
    1. **Juvenile Fish Facilities – Fish Passage Season (April 1 – November 30)**
       1. **STSs and VBSs.**

Operate STSs from April 1 through November 30 for juvenile fish passage, and from December 1 through December 15 for adult fallbacks. Do not operate units without a full complement of rotating STSs except to be in compliance with other coordinated fish measures.

Inspect each STS, VBS, and orifice once per month or every 720 hours run-time. Video inspections are acceptable. More frequent inspections may be required under the following conditions: deterioration of fish condition, increased debris load in JBS, or other indications of STS or VBS malfunction or failure.

Operate Unit 2 when Unit 1 is out of service for STS inspection.

Monitor each STS amp and/or watt meter readings at least once per shift.

If an STS or VBS is damaged, plugged or non-operational, follow procedures in **section 3**.

Include inspection reports in weekly fishway reports and provide to FPOM.

* + - 1. **Gatewells and Orifices.**

Open all gatewell orifices April 1 through December 15.

Inspect all STS gatewells daily.

Clean gatewells before the gatewell water surface becomes 50% covered with debris. If due to the debris volume it is not possible to keep the gatewell surface at least 50% clear, clean gatewells at least once daily. Do not operate turbines that have a gatewell fully covered with debris except to be in compliance with other coordinated fish measures, and then only on a “last-on/first-off” basis. During cleaning, close the powerhouse gatewell orifices. After gatewell de-barking, cycle the orifice in that gatewell. Check gatewell drawdown.

When using a dip basket for gatewell cleaning, coordinate with SMF personnel.

Monitor and record juvenile mortality numbers in all gatewells as potential indicators of gatewell environment problems. Include mortality estimates in the weekly status reports.

Measure gatewell drawdown across the trashrack at least once per week. Remove debris from forebay and trashracks as required to maintain gatewell drawdown < 1.5’. If VBS drawdown reaches 1.2’, inspect the screen and prepare to clean as necessary.

Close and open each orifice three times daily, or more frequently as determined by the Project Biologist if necessary due to heavy debris accumulation in gatewells.

If a unit goes out of service, keep orifices open in the associated gatewells unless that gatewell is dewatered.

Inspect orifice lights daily to ensure they are operating. Replace all burned out orifice lights within 24 hours.

From April 1 through August 1, rake Units 1–5 monthly and Units 6–10 *or* 11–16 every other month. After August 1, rake units as determined necessary by ROV inspection, or as needed to maintain gatewell drawdown in criteria. Perform additional raking whenever trash accumulations are suspected because of increased differential ≥ 1.5’ across the trash racks, or as determined by the Project Biologist in response to increased juvenile fish descaling at the dam, deteriorating fish condition observed at the SMF, or increased accumulation of tumbleweeds in the forebay.

During raking, close the gatewell orifices of the unit being raked.

If debris loads are obvious in the forebay, rake trash in front of the affected unit(s) weekly until the debris is removed. Debris accumulations in the forebay of 300 feet or more in any direction from the face of the dam will be removed within 48 hours. Continue debris removal efforts until the debris is cleared.

Make best efforts to keep all petroleum out of gatewells. Project environmental section will determine cleanup efforts if needed. Regardless of unit operating status, oil accumulations will be dealt with promptly.

Maintain the water level in the bypass conduit between 4.0’ and 5.0’ as measured at Unit 16.

* + - 1. **Smolt Monitoring Facility (SMF)**. From April 1–September 15, Project fish personnel will monitor the SMF 24 hours/day, 7 days/week, to ensure proper functioning and to respond quickly in the event of an emergency. On-duty staff will perform a walking inspection of the entire SMF system every two hours to ensure safe fish passage conditions. The system will be fully staffed while the SMF is in operation (i.e., crest gate deployed and secondary dewatering structure receiving fish-laden flow). To ensure proper function of sampling systems, staff will pay particular attention to the following:

Dewatering facilities, including screens, free of holes or gaps, and the screen cleaner brush system;

All valves and auxiliary water systems;

Flushing water valves and perforated plates;

All gates, including crest, tainter, switch, and rotating gates;

Fish/debris separator, including perforated plates and adult passage chamber;

PIT-tag detectors;

All sampling building systems, including holding tanks, valves, and conduits;

During low to normal debris loads, the Primary Dewatering Screen (PDS) sweepers will be cycled twice per shift (six times per day). If higher debris loads, the frequency of screen sweeper cycling will be increased as determined by the Project Fisheries inspection.

The fish/debris separator will be visually inspected every 30 minutes to prevent injury and/or mortality to fish. During high debris loading periods (likely during spring runoff), additional personnel may be required to keep the separator free of any obstruction to fish passage. The Project Biologist will decide to assign a person to remove debris from the separator on a shift basis (possibly 24 hours/day presence) for as long as necessary to ensure the safety of passing fish.

When river temperatures are ≥ 70°F, all fish handling to remove adult fish from the PDS area will be coordinated through FPOM.

* + - 1. **Temporary Spillway Weirs (TSWs).**

John Day Dam has two temporary, or top, spillway weirs (TSWs) that provide surface passage routes for fish via spillbays 18 and 19. When open, each TSW spills approximately 9.7 kcfs. Opening and closing the TSWs requires a crew and gantry crane and must be done during daylight hours as weather allows.

Both TSWs will be installed as early as possible on the first day of spring spill and operated throughout spring and summer spill. Spill patterns with and without TSWs are defined in **Table JDA-8** and **Table JDA-9**, respectively.

During high flows, TSW removal is recommended before river flow exceeds 685 kcfs.

Both TSWs will be closed as late as possible on the last normal work day of summer spill (no later than August 31). Spill for juvenile fish passage will be maintained through midnight on August 31, pursuant to the FOP (**Appendix E**).

* + - 1. **Avian Predation Management.** Operate in accordance with the *Predation Monitoring and Deterrence Action Plans* for John Day Dam in **Appendix L**, Table 1 and section 4. Avian monitoring at John Day Dam will occur daily during the adult and juvenile fish passage season and hazing will occur daily from April 10 through July 31.
  1. Operating Criteria - Adult Fish Facilities
     1. **Adult Fish Facilities - Winter Maintenance Period (December 1 – end of February)**
        1. Operate according to criteria during adult fish passage season in **section 2.4.2** below, except facilities may be dewatered or operated out of criteria for maintenance or repair. Outage periods will be minimized to the extent practicable. Only one of the two adult fish passage facilities may be out of service at a time. The other facility must be operated within passage season criteria unless otherwise coordinated with FPOM. However, Unit 2 may be operated in place of Unit 1 without special coordination when the south fishway is in service.
        2. Inspect and calibrate all staff gauges, water level sensors, and indicators. Repair and/or clean where necessary.
        3. Dewater and inspect all ladders and other dewatered sections of fish facilities for projections, debris, or plugged orifices that could injure or delay fish. Repair as needed.
        4. Inspect ladder exits for debris and clean when necessary.
        5. At the end of the adult fish counting season (see **Table JDA-3**), pull picket leads at counting stations and adjust crowders so that the counting slots are fully opened (this should be done shortly after adult fish counting ends). Reinstall picket leads at counting stations prior to watering up ladders during maintenance.
        6. Repair or, when necessary, upgrade netting and padding at the top of the north fish ladders to address the fish jumping problem in this area.
        7. Maximum head on attraction water intakes and trash racks at all ladder exits is 0.5'. Remove debris when significant amounts accumulate.
     2. **Adult Fish Facilities – Adult Fish Passage Season (March 1 – November 30).**
        1. Maintain staff gauges and water level indicators in readable condition at all water levels encountered during the fish passage season and check calibration weekly. When necessary, clean and/or recalibrate instruments as soon as practicable.
        2. Maintain water depth over fish ladder weirs at 1.0’ ±0.1’. When the adult shad count at Bonneville Dam exceeds 5,000/day, increase water depth to 1.3’ ±0.1’.
        3. Maintain main entrance weir depths at 8’ or greater below tailwater. Maintain tailwater elevation above 158’ msl to stay within criteria operating range for entrance weirs.
        4. Maintain head on all entrances in the range of 1’–2’ (1.5’ optimum). When unable to achieve head criteria, refer to **section 3.2**.
        5. Open floating orifice gates 1, 2, 18 and 19, and operate three fish pumps to maintain fishway criteria. The entrance gate should be submerged 8’ deep or greater to be in criteria.
        6. Maximum head on attraction water intakes and trashracks at all ladder exits is 0.5’, with a maximum head on all picket leads of 0.3'. Remove significant debris build up.
        7. Measure fishway channel water velocities at least three times per week (daily preferred) during adult fish passage season as part of the fishway inspection program. Floats will be timed through all fishway channels that are supplemented by auxiliary water and results reported in the project weekly fishway status report. Maintain water velocity in the range of 1.5–4.0 feet per second (fps), 2 fps optimum, in all channels and the lower ends of fish ladders that are below the tailwater.
        8. **North Fishway**. Maintain netting and padding for the North fishway to address the adult salmonid jumping problem. All holes in the netting large enough to catch or allow escapement of an adult salmonid must be closed.
        9. **South Fishway.** Operate entrance weir SE-1. Provide adult attraction flow from August 15 through November 30 by spilling from Bay 2 open one stop (1.5 kcfs) during daylight hours defined in **Table JDA-5**.
        10. **Powerhouse.** Operate entrances NE-1 and NE-2. Operate four powerhouse floating orifices, 1, 2, 18, and 19, and open associated auxiliary water diffusers (see also **section 2.4.2.4**). From 0400–2000 hours, operate Unit 1 near 100 MW (±10) to provide best entrance conditions. If additional load is required by BPA, Unit 1 may be operated above 100 MW, but it should be the last unit brought up to full load when demand increases and the first unit to reduce when demand decreases (see **Appendix C - Load Shaping Guidelines**).
        11. **Fishway Temperature Monitoring.**
            1. Measure water temperatures at the count stations of each ladder and include the weekly means in the status report. When water temperature reaches 70°F, all fish handling activities will be coordinated through FPOM prior to any action to verify protocols that will be followed.
            2. From June 1 through September 30, measure water temperature at adult fishway entrances and exits and submit data to the Fish Passage Center (FPC) weekly for posting online.[[4]](#footnote-4) Ensure the location of the monitors meets the following criteria:

Within 10 meters of all shore-oriented entrances and exits.

Entrance monitor within 1 meter above the ladder floor and at least 10 meters downstream of ladder diffusers, if possible, to allow for sufficient mixing with surface water.

Exit monitor within 1 meter above the ladder floor and above all diffusers to allow for sufficient mixing with surface water.

If an existing temperature monitoring location is proposed to be used for either the exit or entrance, verify that the site accurately reflects water temperature within 10 meters of the entrance or exit.

* + - 1. **Adult Fish Counting.**

The current adult fish counting schedule is in **Table JDA-3**.

Crowder ranges are: JDA-North = 18”–28”; JDA-South = 18”–30”

When not counting, or if counting is temporarily discontinued due to unscheduled events, open the crowder to full count slot width. The crowder may remain in operating position during the counter’s hourly 10-minute break.

During counting, open the crowder as far as possible to allow accurate counting, at least 18”. Do not close to less than 18” inches while counting. This will usually occur during high turbidity conditions to maintain count accuracy. If passage is impaired by narrow count slot conditions, open the count slot until proper passage conditions are achieved, despite reduced count accuracy. Project biologists, FFU, and the fish count supervisor shall coordinate to achieve optimum count slot passage and/or count accuracy conditions.

* 1. Fish Facilities Monitoring & Reporting
     1. **Monitoring.** 
        1. During fish passage season, inspect fish passage facilities at least twice per day, seven days a week to ensure operation according to established criteria.
        2. During the winter maintenance period, inspect fish facilities once per day, seven days a week. More frequent inspections of some facility components will occur pursuant to critieria in this document.
        3. Additional fishway inspections may be performed by FFU and fish agencies.
        4. Report results of all inspections and the readiness of the facilities for operation to FPOM at the meeting immediately prior to the fish passage season.
        5. Continue to implement the zebra mussel monitoring program. These organisms are a serious problem elsewhere in the country and may become introduced into the Columbia River basin. Inspections should also be made when dewatering project facilities.
     2. **Reporting.** 
        1. **Weekly Reports.** Project biologists shall prepare weekly reports throughout the year summarizing project and fish facility operations for each week (Sunday through Saturday), along with an evaluation of resulting fish passage conditions. The reports will be e-mailed to CENWP-OD, CENWD-PDW-R (RCC), and other interested parties as soon as possible the following week. The weekly reports shall include:

Out-of-criteria situations and subsequent corrective actions;

Equipment malfunctions, breakdowns, or damage, with a summary of resulting repairs;

Adult fishway control calibrations;

STS and VBS inspections;

AWS closures (i.e. cleaning times);

Unusual activities at the project that may affect fish passage.

* + - 1. **In-Season.** Any adverse or negative impact to fish or fishways shall be reported in a *Memorandum for the Record* (MFR) prepared by Project biologists and sent to FPOM by the next working day, pursuant to the coordination process and template in **FPP Chapter 1 – Overview, section 2.3.2**.
      2. **Annual Report.** Project biologists shall prepare an annual report by January 31 each year, summarizing fish facility operations for the previous year’s winter maintenance period and fish passage season, December 1 through November 30. The annual report will also include all actions taken to discourage avian predation at the project, with an overview of the effectiveness of the actions. The annual report will be provided to CENWP-OD in time for distribution to FPOM members at the February meeting.

1. Fish Facilities Maintenance
   1. Fish Facilities Routine Maintenance
      1. Routine maintenance of fish facilities will be conducted when fish passage has been documented to be at its lowest, to the extent practicable, to minimize fish impacts. Maintenance that occurs during juvenile or adult passage season that may affect fish passage will be included in the weekly reports, per **section 2.5.2**. If maintenance requires operating outside of FPP criteria, the work will be coordinated with FPOM per the procedures defined in **FPP Chapter 1–Overview, section 2.3**.
      2. **Submersible Traveling Screens (STS)**. The STS system may receive preventive maintenance or repair any time of the year as necessary. Most maintenance will occur during the winter maintenance period when all STSs may be removed from intakes. From April 1–December 15, a turbine unit cannot operate without a full complement of functioning STSs.
      3. **Juvenile Bypass System (JBS)**. The JBS facilities may receive preventive maintenance at any time of the year as necessary in coordination with FPOM. During the juvenile fish passage season, this will normally be out-of-water work (e.g., maintenance of automatic systems, air lines, electrical systems, and monitoring equipment). During the winter maintenance period, the system is dewatered and visually inspected in all accessible areas for damaged equipment and areas that may cause potential problems to juvenile fish. Identified problems will be repaired by project maintenance or the contractor as soon as possible. Extended repair projects will be coordinated through FPOM.
      4. **Turbines & Spillbays**. Routine maintenance and repair of project turbines and spillbays is a regular and recurring process that requires extended outages (see **Turbine Maintenance section 4.3** and **Dewatering Plans section 5**). If maintenance requires operating outside of FPP criteria, the work will be coordinated with FPOM. Certain turbine and spillbay discharges are secondarily used to attract adult fish to fishway entrances, to keep predator fish from accumulating near juvenile release sites, and to move juveniles downstream away from the project. The maintenance schedules for these turbines and spillbays will reflect equal weight given to fish, power, and water management and will be coordinated with the appropriate fish agencies. Units 1, 2, and 5 should not be scheduled for maintenance during fish passage season.
      5. **Fishway Auxiliary Water Systems**. John Day Dam has tailwater pump auxiliary water systems. Preventive maintenance and normal repair are carried out throughout the year. Trash racks for the AWS intakes will be raked when drawdown exceeds criteria. When practicable, rake trash racks during the time of day when fish passage is least affected. During the annual navigation lock maintenance outage, the north fish ladder auxiliary water is shut off for about half a day. This is required to allow divers to clean off the navigation lock discharge sill so that a bulkhead can be placed.
      6. **Adult Fish Collection Systems.** Preventive maintenance and repair occurs throughout the year as needed. During the adult fish passage season, this maintenance will not result in failing to achieve fishway criteria unless coordinated with FPOM. During the winter maintenance period, an inspection will occur through dewatering or divers per discretion of the Project Biologists. One additional underwater diver/ROV will occur August 1-15. Timing of this inspection will be coordinated through FPOM. The Project Biologist or alternate Corps fish personnel will attend all dewatering and inspection activities potentially involving fish (**section 6**).
      7. **Adult Ladders and Count Stations.** Adult fish ladders are dewatered once each year during the winter maintenance period. Unless specially coordinated, only one ladder will be dewatered at a time with the other ladder operating within criteria. During this time, the ladders are inspected for necessary maintenance needs and potential fish passage problems (e.g., blocked orifices, projections into the fishway that may injure fish, unstable weirs, damaged picket leads, exit gate problems, loose diffuser gratings, unreadable or damaged staff gauges, defective diffuser valves, and malfunctioning equipment at the counting stations). Potential problems identified throughout the passage year that do not impact fish passage, as well as those identified during the dewatered period, are repaired. Rake trash racks at ladder exits when criteria are exceeded. When practicable, rake trash racks during the time of day when fish passage would be least impacted. Clean fish count station windows, light panels, and crowder panels as needed to achieve accurate counts and, when practicable, during the time of day when fish passage is least impacted. Inspect north netting on ladders daily to prevent fish leaping and maintain as necessary. Include inspection summaries in the weekly report.
   2. Fish Facilities Non-Routine Maintenance
      1. Non-routine or unscheduled fish facility maintenance that may impact fish passage or operation of fish facilities (e.g., repair of diffuser gratings, etc.) shall be coordinated through FPOM on a case-by-case basis by Project and CENWP-OD biologists, per the coordination process described in **FPP Chapter 1–Overview, section 2.3**. The CENWP-OD biologists will be notified as soon as possible after it becomes apparent that non-routine maintenance or repairs are required. The Operations Project Manager has the authority to initiate work prior to notifying CENWP-OD when delay of work will result in unsafe situations for people, property, or fish.
      2. Non-routine maintenance that affects fish passage will be included in the weekly reports.
      3. **Juvenile Bypass System (JBS).**
         1. The JBS is automatically controlled. If the automatic system fails, operate manually until automation is repaired.
         2. If the orifices become plugged with debris, do not operate the turbine until it has been cleaned.
         3. If an STS or VBS is found to be damaged or malfunctioning in an operating unit, the unit will be regarded as an unscreened unit. The screen will be repaired or replaced before returning the unit to service.
         4. If the bypass system fails in the powerhouse conduit, tainter gate, or transportation outfall making the system unsafe for fish, a decision will be made in coordination with FPOM. During this emergency operating mode, minimize power generation to the extent practicable. If this operating mode is expected to last longer than four days, sequentially shut down all units required for generation, salvage fish from gatewells, remove STSs, and restart the unit. Close the orifice gates during this process.
      4. **Turbines and Spillbays.**
         1. Whenever Unit 1 is not operating, operate Unit 2 for adult attraction.
         2. Between September 15 and the end of February, spillbay 2 may be closed for up to one workday for maintenance activities. During the outage, operate spillbay 3 for adult attraction flow.
         3. If a spill gate becomes inoperable, the operators will make the necessary changes to accommodate spill and then immediately notify the operations supervisor and Project Biologist to determine the best spill pattern until repairs can be made. This interim operation shall be coordinated with the FPOM through the District biologist who will provide additional guidance to the project.
      5. **Fishway Auxiliary Water Systems**. The fishway auxiliary water systems are mostly automated. If the automatic system fails, manually operate the system to maintain the fish facility within criteria until the automatic system is repaired. When this operation becomes necessary, project personnel will increase the surveillance of the adult system to ensure that criteria are being met. In the event of an AWS failure during adult passage season, coordinate with FPOM to determine the best operation.
         1. **South Ladder:** Assuming all three auxiliary water turbines are being used to meet criteria, operate as follows in the event of a failure of one or more turbines:
            1. If one turbine fails, increase the output of the two remaining turbines to meet adult fishway criteria.
            2. If two turbine units fail, operate the adult fish facility as follows until a fishway head of 1' is achieved:

Increase discharge of remaining unit to maximum capacity;

Close NE-1;

Leave NE-2 at a depth of 8’;

Close remaining floating submerged orifice gate entrances starting at north end;

Leave south powerhouse entrance weir (SE-1) at 8' depth below tailwater surface.

If criteria are still not achieved, reduce entrance weirs depth to 6’, then to 4’ if necessary, until more auxiliary water is available. Then reverse the above procedure.

* + - * 1. If all three turbine units fail, operate as follows until repairs can be made:

Open SE-1 with the weir crest 6' below the tailwater surface;

Close NE1 and NE2;

Place cross-channel bulkheads in powerhouse collection channel between Units 2 and 3;

Close floating orifice gate in front of Unit 2, leaving the floating orifice gate in front of Unit 1 open.

* + - 1. **North Ladder:** The six AWS pumps installed in 2011 are capable of achieving the optimal attraction criteria of 1.5' at all tailrace elevations. There is a built-in contingency as one of the six pumps is always spare and will be automatically started by PLC in case of another pump's failure.
    1. **Powerhouse and Spillway Fish Collection Systems.** John Day Dam contains several types of fishway entrances. If failures occur, in most cases the entrance can be operated manually by project personnel until repaired. When this operation becomes necessary, project personnel will increase surveillance of the adult system to ensure criteria are being met. If the failure will not allow the entrance to be operated manually, the gate will be maintained in an operational position to the extent possible. If this is not possible, the entrance will be repaired expediently and the entrance will be returned to manual or automatic control at the earliest possible date.
    2. **Adult Ladders and Count Stations**. Pickets with excessive spacing (>1"), erosion of concrete around the picket leads, or missing pickets may allow fish into areas where they cannot escape. The north count station upstream picket leads have an exit hatch that can be opened to allow fish to escape. Repair will be required for picket lead failure at the south count station. In the instances of picket lead failure or concrete erosion, the timing and method of repair will depend upon the severity of the problem. The decision of whether or not to dewater the fishway for repairs will be made in coordination with FPOM.
    3. **Diffuser Gratings.** Diffuser chambers for adding auxiliary water to ladders and collection channels are covered by gratings attached by several methods. Diffuser gratings are normally inspected during winter maintenance to ensure integrity. Inspections are done by either dewatering the fishway and/or collection channel, or by using video cameras and divers or other methods to inspect the gratings underwater. Diffuser gratings may come loose during fish passage season due to a variety of reasons. Daily inspections of the ladders and collection systems should include looking for flow changes that may indicate problems with diffuser gratings. If a diffuser grating is known to or suspected of having moved, creating an opening into a diffuser chamber, efforts must immediately be taken to correct the situation and minimize impacts on adult fish in the fishway. If possible, a video inspection should be made as soon as possible to determine the extent of the problem. If diffusers gratings are found to be missing or displaced, close the associated diffuser and develop a method of repair as coordinated with FPOM. Repair as quickly as possible unless coordinated differently.

1. TURBINE UNIT OPERATION & MAINTENANCE
   1. Turbine Unit Priority Order
      1. Turbine units will be operated in the order of priority defined in **Table JDA-6**, including time during synchronous condensing. If a unit is out of service for maintenance or repair, the next unit in the priority order shall be operated. Unit priority order may be coordinated differently for fish research, construction, or project maintenance.

Table JDA-6. John Day Dam Turbine Unit Priority Order.

|  |  |
| --- | --- |
| **Season** | **Unit Priority Order\*** |
| March 1 – November 30  Fish Passage Season | * With TSWs = 5, 1, 3, 16, 14, 12, 10, 8, 15, 2, 11, 7, 4, 13, 9, 6 * No TSWs = 1–4 any order, then 5–16 any order |
| December 1 – end of February  Winter Maintenance Period | Any Order |

\*When a main unit is not available, the paired adjacent unit will be used to comply with requested priority.

* 1. Turbine Unit Operating Range
     1. Turbine unit flow and power output at the lower and upper limits of the ±1% peak efficiency range, and at the operating limit, are defined in **Table JDA-7**, except units with locked runner blades (non-adjustable) are in **Table JDA-7-A**.
     2. **In-Season (April 1–October 31).** As defined in the *BPA Load Shaping Guidelines* (**Appendix C**), all units will be operated within ±1% of peak turbine efficiency (1% range) to maximize survival of juvenile fish that pass through the turbines. If necessary to operate turbines outside the 1% range, units will be operated in order from north to south since juvenile passage through turbines decreases from south to north, making inefficient operation of Unit 16 least likely to impact fish. However, allowance will also be given to special project requirements for stable voltage control that requires load distribution between transformer banks. In-season operation outside the 1% range shall be recorded by Project personnel and provided to BPA on a weekly basis according to the *Guidelines*. Operation outside the 1% range may be necessary to:

Meet BPA load requests made pursuant to BPA's policy, statutory requirements, and *Load Shaping Guidelines* (**Appendix C**);

If the draft tube is to be dewatered (**section 4.3.2**), the unit will be operated at full load > 1% (or at speed-no-load < 1% if not possible to load) for a minimum of 15 minutes prior to installing tail logs in order to flush fish from the unit;

Operate a turbine unit solely to provide station service; or

Comply with other coordinated fish measures.

* + 1. **Off-Season (November 1–March 31).** While not required to do so in the off-season, turbines will normally run within the 1% range since it is the optimum point for maximizing energy output of a given unit of water over time. Operation outside the 1% range is allowed if needed for power generation or other needs.
  1. Turbine Unit Maintenance
     1. Turbine unit maintenance schedules will be reviewed by Project and District biologists for fish impacts. If maintenance requires operating outside of FPP criteria, the work will be coordinated with FPOM per the procedures defined in **FPP Chapter 1–Overview, section 2.3**.
     2. If the draft tube is to be dewatered (see **section 6.5**), the unit will be operated at full load above the 1% range (or at speed-no-load below the 1% range if not possible to load) for a minimum of 15 minutes prior to installing tail logs to flush fish from the unit.
     3. **Operational Testing**. Some types of turbine maintenance require testing turbine operation throughout its full range before and after maintenance. Operational testing of a unit under maintenance is in addition to a unit in run status required for power plant reliability. Operational testing may deviate from FPP priority order and may require water that would otherwise be used for spill if the project is operating at minimum generation requirements. Water for operational testing will be used from powerhouse allocation when possible and diverted from spill only to the extent necessary to maintain generation system reliability.

Pre-Maintenance: Units may be operationally tested for up to 30 minutes by running at speed-no-load and various loads within the 1% range for pre-maintenance measurements and testing, and to allow all fish to move through the unit as defined in **section 6.5.2**.

Post-Maintenance: After maintenance or repair, units may be operationally tested while in maintenance or forced outage status for up to a cumulative time of 30 minutes (within 1% range) before returning to operational status.

* + 1. Wicket gate opening for functional testing of a watered-up unit will be less than 15 minutes total open time.

Table JDA-7. John Day Dam Turbine Unit Power (MW) and Flow (cfs) at ±1% of Peak Turbine Efficiency (Lower and Upper Limits of 1% Range) and Operating Limits. a

|  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **Project** | **JDA Units 1–16 With STS b** | | | | | | **JDA Units 1–16 No STS b** | | | | | |
| **Head** | **1% Lower Limit** | | **1% Upper Limit** | | **Operating Limit c** | | **1% Lower Limit** | | **1% Upper Limit** | | **Operating Limit c** | |
| **(feet)** | **MW** | **cfs** | **MW** | **cfs** | **MW** | **cfs** | **MW** | **cfs** | **MW** | **cfs** | **MW** | **cfs** |
| **80** | 65.4 | 11,338 | 118.0 | 20,472 | 129.9 | 23,194 | 71.7 | 12,305 | 122.8 | 21,074 | 129.9 | 22,684 |
| **81** | 66.7 | 11,416 | 120.8 | 20,671 | 132.1 | 23,228 | 73.2 | 12,391 | 125.7 | 21,290 | 132.1 | 22,697 |
| **82** | 68.1 | 11,492 | 123.6 | 20,864 | 134.3 | 23,261 | 74.7 | 12,473 | 128.7 | 21,500 | 134.3 | 22,710 |
| **83** | 69.4 | 11,566 | 126.4 | 21,052 | 136.5 | 23,292 | 76.1 | 12,554 | 131.6 | 21,703 | 136.5 | 22,720 |
| **84** | 70.8 | 11,638 | 129.1 | 21,234 | 138.7 | 23,321 | 77.6 | 12,631 | 134.6 | 21,901 | 138.7 | 22,730 |
| **85** | 72.1 | 11,707 | 131.9 | 21,411 | 140.9 | 23,349 | 79.1 | 12,707 | 137.5 | 22,093 | 140.9 | 22,738 |
| **86** | 72.9 | 11,692 | 134.7 | 21,593 | 142.7 | 23,282 | 80.0 | 12,690 | 140.1 | 22,223 | 142.7 | 22,722 |
| **87** | 73.7 | 11,676 | 137.5 | 21,770 | 144.5 | 23,214 | 80.9 | 12,674 | 142.6 | 22,349 | 144.5 | 22,704 |
| **88** | 74.5 | 11,661 | 140.2 | 21,942 | 146.2 | 23,145 | 81.7 | 12,657 | 145.1 | 22,471 | 146.2 | 22,684 |
| **89** | 75.3 | 11,646 | 143.0 | 22,110 | 148.0 | 23,074 | 82.6 | 12,641 | 147.6 | 22,591 | 148.0 | 22,662 |
| **90** | 76.1 | 11,632 | 145.8 | 22,274 | 149.7 | 23,001 | 83.5 | 12,625 | 150.2 | 22,707 | 149.7 | 22,638 |
| **91** | 77.0 | 11,622 | 146.9 | 22,164 | 151.1 | 22,917 | 84.5 | 12,616 | 151.7 | 22,656 | 151.1 | 22,562 |
| **92** | 77.9 | 11,613 | 148.0 | 22,057 | 152.5 | 22,831 | 85.5 | 12,606 | 153.2 | 22,606 | 152.5 | 22,484 |
| **93** | 78.8 | 11,604 | 149.1 | 21,951 | 153.8 | 22,743 | 86.4 | 12,596 | 154.8 | 22,556 | 153.8 | 22,403 |
| **94** | 79.7 | 11,595 | 150.2 | 21,848 | 155.1 | 22,652 | 87.4 | 12,586 | 156.3 | 22,507 | 155.1 | 22,321 |
| **95** | 80.6 | 11,585 | 151.3 | 21,746 | 155.2 | 22,383 | 88.4 | 12,576 | 157.8 | 22,459 | 155.2 | 22,062 |
| **96** | 81.7 | 11,604 | 151.6 | 21,532 | 155.2 | 22,115 | 89.6 | 12,597 | 158.2 | 22,243 | 155.2 | 21,797 |
| **97** | 82.8 | 11,623 | 151.8 | 21,323 | 155.2 | 21,852 | 90.8 | 12,617 | 158.5 | 22,032 | 155.2 | 21,538 |
| **98** | 83.8 | 11,640 | 152.1 | 21,118 | 155.2 | 21,595 | 92.0 | 12,636 | 158.8 | 21,826 | 155.2 | 21,284 |
| **99** | 84.9 | 11,657 | 152.4 | 20,917 | 155.2 | 21,343 | 93.1 | 12,655 | 159.2 | 21,623 | 155.2 | 21,035 |
| **100** | 86.0 | 11,674 | 152.7 | 20,720 | 155.2 | 21,096 | 94.3 | 12,673 | 159.5 | 21,425 | 155.2 | 20,792 |
| **101** | 86.9 | 11,675 | 154.9 | 20,800 | 155.2 | 20,852 | 95.3 | 12,675 | 161.8 | 21,507 | 155.2 | 20,554 |
| **102** | 87.9 | 11,677 | 157.1 | 20,877 | 155.2 | 20,613 | 96.4 | 12,676 | 164.1 | 21,587 | 155.2 | 20,321 |
| **103** | 88.8 | 11,678 | 159.3 | 20,953 | 155.2 | 20,378 | 97.4 | 12,678 | 166.4 | 21,666 | 155.2 | 20,092 |
| **104** | 89.7 | 11,679 | 161.5 | 21,027 | 155.2 | 20,149 | 98.4 | 12,679 | 168.7 | 21,742 | 155.2 | 19,868 |
| **105** | 90.6 | 11,680 | 163.7 | 21,100 | 155.2 | 19,923 | 99.4 | 12,680 | 171.0 | 21,817 | 155.2 | 19,649 |
| **106** | 91.4 | 11,658 | 165.2 | 21,084 | 155.2 | 19,711 | 100.2 | 12,656 | 172.6 | 21,801 | 155.2 | 19,442 |
| **107** | 92.1 | 11,637 | 166.7 | 21,068 | 155.2 | 19,503 | 101.0 | 12,633 | 174.2 | 21,785 | 155.2 | 19,239 |
| **108** | 92.8 | 11,615 | 168.3 | 21,052 | 155.2 | 19,299 | 101.8 | 12,610 | 175.8 | 21,768 | 155.2 | 19,040 |
| **109** | 93.6 | 11,594 | 169.8 | 21,036 | 155.2 | 19,098 | 102.6 | 12,587 | 177.4 | 21,752 | 155.2 | 18,845 |
| **110** | 94.3 | 11,574 | 171.3 | 21,021 | 155.2 | 18,901 | 103.5 | 12,565 | 179.0 | 21,736 | 155.2 | 18,653 |

1. Values provided by HDC (Nov 2002). Flow (cfs) was calculated based on turbine efficiency, project head, and power output (MW).
2. Units 3, 4, 8, 9, 10, 11, and 14 have locked blades and a restricted operating range of approximately 17-19 kcfs. See Table JDA-7-A below for operating ranges of each locked-blade unit.
3. “Operating Limit” (added Feb 2018) is the maximum safe operating point based on cavitation or generator limit. JDA units have a generator limit that restricts turbine output at higher heads. Values shaded in gray indicate the Operating Limit is below the 1% Upper Limit.

Table JDA-7-A. Operating Range Values for John Day Turbine Units 3, 4, 8, 9, 10, 11, and 14 with Locked Runner Blades

(Non-Adjustable). a

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **Project Head (feet)** | **Unit 3 w/ Blades Hydraulically Locked at 29.1° (Sep 2020)** | | | | | | | | **Unit 4 w/ Blades Welded at 29.1° (May 2016)** | | | | | | | |
| **With STS** | | | | **No STS** | | | | **With STS** | | | | **No STS** | | | |
| **Lower Limit** | | **Upper Limit** | | **Lower Limit** | | **Upper Limit** | | **Lower Limit** | | **Upper Limit** | | **Lower Limit** | | **Upper Limit** | |
| **MW** | **cfs** | **MW** | **cfs** | **MW** | **cfs** | **MW** | **cfs** | **MW** | **cfs** | **MW** | **cfs** | **MW** | **cfs** | **MW** | **cfs** |
| 80 | 104.8 | 18,339 | 109.3 | 19,139 | 105.2 | 18,204 | 109.8 | 18,995 | 103.1 | 18,040 | 108.0 | 18,909 | 103.5 | 17,912 | 108.5 | 18,771 |
| 81 | 106.2 | 18,317 | 110.6 | 19,087 | 106.6 | 18,183 | 111.1 | 18,944 | 104.4 | 18,019 | 109.3 | 18,857 | 104.9 | 17,892 | 109.7 | 18,720 |
| 82 | 107.5 | 18,296 | 111.9 | 19,036 | 108.0 | 18,162 | 112.3 | 18,893 | 105.8 | 17,998 | 110.5 | 18,806 | 106.3 | 17,871 | 111.0 | 18,670 |
| 83 | 108.9 | 18,274 | 113.2 | 18,985 | 109.4 | 18,141 | 113.6 | 18,843 | 107.1 | 17,977 | 111.8 | 18,756 | 107.6 | 17,850 | 112.3 | 18,621 |
| 84 | 110.3 | 18,252 | 114.4 | 18,934 | 110.8 | 18,119 | 114.9 | 18,793 | 108.5 | 17,955 | 113.0 | 18,706 | 109.0 | 17,829 | 113.5 | 18,572 |
| 85 | 111.7 | 18,230 | 115.7 | 18,885 | 112.1 | 18,097 | 116.2 | 18,744 | 109.9 | 17,933 | 114.3 | 18,657 | 110.4 | 17,808 | 114.8 | 18,523 |
| 86 | 113.4 | 18,279 | 117.2 | 18,902 | 113.8 | 18,134 | 117.7 | 18,749 | 111.5 | 17,969 | 115.8 | 18,662 | 112.0 | 17,843 | 116.3 | 18,528 |
| 87 | 115.1 | 18,326 | 118.8 | 18,920 | 115.6 | 18,169 | 119.3 | 18,754 | 113.2 | 18,003 | 117.5 | 18,687 | 113.7 | 17,877 | 118.0 | 18,554 |
| 88 | 116.8 | 18,372 | 120.4 | 18,936 | 117.3 | 18,202 | 120.8 | 18,758 | 114.9 | 18,036 | 119.2 | 18,711 | 115.4 | 17,910 | 119.7 | 18,578 |
| 89 | 118.5 | 18,417 | 121.9 | 18,952 | 119.0 | 18,234 | 122.4 | 18,761 | 116.5 | 18,067 | 120.8 | 18,734 | 117.1 | 17,942 | 121.4 | 18,601 |
| 90 | 120.2 | 18,397 | 123.5 | 18,902 | 120.7 | 18,264 | 124.0 | 18,763 | 118.2 | 18,097 | 122.0 | 18,674 | 118.7 | 17,972 | 122.5 | 18,542 |
| 91 | 121.6 | 18,395 | 125.2 | 18,931 | 122.1 | 18,263 | 125.7 | 18,792 | 119.6 | 18,096 | 123.7 | 18,703 | 120.2 | 17,971 | 124.2 | 18,571 |
| 92 | 123.1 | 18,393 | 126.9 | 18,959 | 123.6 | 18,262 | 127.4 | 18,820 | 121.1 | 18,094 | 125.3 | 18,731 | 121.6 | 17,969 | 125.9 | 18,598 |
| 93 | 124.6 | 18,391 | 128.6 | 18,986 | 125.1 | 18,260 | 129.1 | 18,848 | 122.5 | 18,092 | 127.0 | 18,757 | 123.1 | 17,967 | 127.6 | 18,625 |
| 94 | 126.0 | 18,389 | 130.3 | 19,012 | 126.5 | 18,257 | 130.8 | 18,873 | 124.0 | 18,089 | 128.7 | 18,783 | 124.5 | 17,965 | 129.3 | 18,651 |
| 95 | 127.5 | 18,386 | 132.0 | 19,037 | 128.0 | 18,255 | 132.5 | 18,898 | 125.4 | 18,086 | 130.4 | 18,807 | 126.0 | 17,962 | 131.0 | 18,675 |
| 96 | 129.0 | 18,400 | 133.6 | 19,051 | 129.5 | 18,269 | 134.1 | 18,912 | 126.9 | 18,100 | 132.0 | 18,821 | 127.5 | 17,976 | 132.5 | 18,689 |
| 97 | 130.5 | 18,413 | 135.2 | 19,064 | 131.1 | 18,283 | 135.7 | 18,925 | 128.4 | 18,114 | 133.5 | 18,834 | 129.0 | 17,990 | 134.1 | 18,702 |
| 98 | 132.1 | 18,426 | 136.7 | 19,076 | 132.6 | 18,296 | 137.3 | 18,938 | 129.9 | 18,127 | 135.1 | 18,846 | 130.5 | 18,003 | 135.7 | 18,714 |
| 99 | 133.6 | 18,439 | 138.3 | 19,088 | 134.2 | 18,308 | 138.9 | 18,949 | 131.4 | 18,139 | 136.6 | 18,858 | 132.0 | 18,015 | 137.2 | 18,726 |
| 100 | 135.1 | 18,451 | 139.9 | 19,099 | 135.7 | 18,320 | 140.4 | 18,961 | 132.9 | 18,151 | 138.2 | 18,869 | 133.5 | 18,027 | 138.8 | 18,737 |
| 101 | 136.4 | 18,428 | 141.4 | 19,099 | 137.0 | 18,297 | 141.9 | 18,960 | 134.2 | 18,128 | 139.7 | 18,868 | 134.8 | 18,004 | 140.3 | 18,737 |
| 102 | 137.7 | 18,404 | 142.9 | 19,098 | 138.2 | 18,274 | 143.4 | 18,960 | 135.4 | 18,105 | 141.1 | 18,868 | 136.0 | 17,982 | 141.7 | 18,736 |
| 103 | 138.9 | 18,381 | 144.3 | 19,097 | 139.5 | 18,252 | 144.9 | 18,959 | 136.7 | 18,082 | 142.6 | 18,866 | 137.3 | 17,959 | 143.2 | 18,735 |
| 104 | 140.2 | 18,359 | 145.8 | 19,095 | 140.8 | 18,229 | 146.4 | 18,958 | 137.9 | 18,060 | 144.1 | 18,865 | 138.5 | 17,937 | 144.7 | 18,734 |
| 105 | 141.5 | 18,336 | 147.3 | 19,094 | 142.1 | 18,207 | 147.9 | 18,956 | 139.2 | 18,038 | 145.6 | 18,864 | 139.8 | 17,915 | 146.2 | 18,732 |
| 106 | 142.3 | 18,262 | 148.7 | 19,076 | 142.9 | 18,133 | 149.3 | 18,938 | 140.0 | 17,965 | 146.9 | 18,846 | 140.7 | 17,843 | 147.5 | 18,715 |
| 107 | 143.2 | 18,189 | 150.1 | 19,058 | 143.8 | 18,061 | 150.7 | 18,920 | 140.9 | 17,893 | 148.2 | 18,828 | 141.5 | 17,772 | 148.9 | 18,697 |
| 108 | 144.1 | 18,117 | 151.4 | 19,040 | 144.7 | 17,990 | 152.0 | 18,903 | 141.7 | 17,822 | 149.6 | 18,810 | 142.4 | 17,702 | 150.2 | 18,680 |
| 109 | 144.9 | 18,047 | 152.8 | 19,022 | 145.5 | 17,920 | 153.4 | 18,885 | 142.6 | 17,753 | 150.9 | 18,792 | 143.2 | 17,633 | 151.6 | 18,662 |
| 110 | 145.8 | 17,978 | 154.1 | 19,004 | 146.4 | 17,852 | 154.8 | 18,868 | 143.4 | 17,685 | 152.3 | 18,775 | 144.1 | 17,566 | 152.9 | 18,645 |
| **Project Head (feet)** | **Unit 8 w/ Blades Welded at 29.4° (March 2017)** | | | | | | | | **Unit 9 w/ Blades Welded at 29.0° (Sep 2015)** | | | | | | | |
| **With STS** | | | | **No STS** | | | | **With STS** | | | | **No STS** | | | |
| **Lower Limit** | | **Upper Limit** | | **Lower Limit** | | **Upper Limit** | | **Lower Limit** | | **Upper Limit** | | **Lower Limit** | | **Upper Limit** | |
| **MW** | **cfs** | **MW** | **cfs** | **MW** | **cfs** | **MW** | **cfs** | **MW** | **cfs** | **MW** | **cfs** | **MW** | **cfs** | **MW** | **cfs** |
| 80 | 105.7 | 18,499 | 109.4 | 19,157 | 106.1 | 18,366 | 109.9 | 19,017 | 102.4 | 17,813 | 107.3 | 18,665 | 102.8 | 17,688 | 107.7 | 18,531 |
| 81 | 107.1 | 18,478 | 110.7 | 19,105 | 107.5 | 18,345 | 111.2 | 18,966 | 103.7 | 17,792 | 108.5 | 18,615 | 104.2 | 17,668 | 109.0 | 18,481 |
| 82 | 108.5 | 18,456 | 112.0 | 19,054 | 108.9 | 18,323 | 112.5 | 18,915 | 105.1 | 17,771 | 109.7 | 18,564 | 105.5 | 17,648 | 110.2 | 18,432 |
| 83 | 109.9 | 18,434 | 113.3 | 19,003 | 110.3 | 18,302 | 113.7 | 18,865 | 106.4 | 17,750 | 111.0 | 18,515 | 106.9 | 17,627 | 111.5 | 18,383 |
| 84 | 111.3 | 18,412 | 114.5 | 18,952 | 111.7 | 18,280 | 115.0 | 18,815 | 107.8 | 17,729 | 112.2 | 18,466 | 108.2 | 17,607 | 112.7 | 18,335 |
| 85 | 112.7 | 18,389 | 115.8 | 18,902 | 113.1 | 18,259 | 116.3 | 18,766 | 109.1 | 17,708 | 113.5 | 18,418 | 109.6 | 17,586 | 114.0 | 18,287 |
| 86 | 114.4 | 18,426 | 117.4 | 18,907 | 114.9 | 18,295 | 117.9 | 18,771 | 110.8 | 17,743 | 115.0 | 18,423 | 111.3 | 17,621 | 115.5 | 18,293 |
| 87 | 116.1 | 18,461 | 119.1 | 18,936 | 116.6 | 18,330 | 119.6 | 18,800 | 112.4 | 17,777 | 116.7 | 18,448 | 112.9 | 17,655 | 117.2 | 18,318 |
| 88 | 117.8 | 18,494 | 120.8 | 18,964 | 118.3 | 18,364 | 121.3 | 18,828 | 114.1 | 17,810 | 118.3 | 18,472 | 114.6 | 17,688 | 118.8 | 18,342 |
| 89 | 119.5 | 18,527 | 122.5 | 18,990 | 120.0 | 18,396 | 123.0 | 18,854 | 115.7 | 17,841 | 120.0 | 18,494 | 116.3 | 17,719 | 120.5 | 18,365 |
| 90 | 121.2 | 18,557 | 123.6 | 18,920 | 121.7 | 18,427 | 124.1 | 18,785 | 117.4 | 17,871 | 121.1 | 18,435 | 117.9 | 17,749 | 121.6 | 18,306 |
| 91 | 122.7 | 18,556 | 125.3 | 18,949 | 123.2 | 18,426 | 125.8 | 18,814 | 118.8 | 17,869 | 122.8 | 18,464 | 119.4 | 17,748 | 123.3 | 18,335 |
| 92 | 124.2 | 18,554 | 127.0 | 18,977 | 124.7 | 18,424 | 127.5 | 18,842 | 120.3 | 17,868 | 124.5 | 18,491 | 120.8 | 17,746 | 125.0 | 18,363 |
| 93 | 125.6 | 18,552 | 128.7 | 19,004 | 126.2 | 18,422 | 129.2 | 18,869 | 121.7 | 17,866 | 126.1 | 18,518 | 122.2 | 17,744 | 126.7 | 18,389 |
| 94 | 127.1 | 18,549 | 130.4 | 19,030 | 127.7 | 18,420 | 131.0 | 18,895 | 123.1 | 17,863 | 127.8 | 18,543 | 123.7 | 17,742 | 128.4 | 18,415 |
| 95 | 128.6 | 18,546 | 132.1 | 19,055 | 129.2 | 18,417 | 132.7 | 18,920 | 124.5 | 17,861 | 129.5 | 18,568 | 125.1 | 17,740 | 130.0 | 18,439 |
| 96 | 130.1 | 18,561 | 133.7 | 19,069 | 130.7 | 18,432 | 134.3 | 18,934 | 126.0 | 17,874 | 131.0 | 18,581 | 126.6 | 17,754 | 131.6 | 18,452 |
| 97 | 131.7 | 18,574 | 135.3 | 19,082 | 132.3 | 18,445 | 135.8 | 18,947 | 127.5 | 17,888 | 132.6 | 18,594 | 128.1 | 17,767 | 133.1 | 18,465 |
| 98 | 133.2 | 18,588 | 136.9 | 19,094 | 133.8 | 18,459 | 137.4 | 18,959 | 129.0 | 17,900 | 134.1 | 18,606 | 129.6 | 17,780 | 134.7 | 18,477 |
| 99 | 134.8 | 18,600 | 138.4 | 19,106 | 135.4 | 18,471 | 139.0 | 18,971 | 130.5 | 17,913 | 135.7 | 18,618 | 131.1 | 17,792 | 136.2 | 18,489 |
| 100 | 136.3 | 18,612 | 140.0 | 19,117 | 136.9 | 18,483 | 140.6 | 18,983 | 132.0 | 17,924 | 137.2 | 18,629 | 132.6 | 17,804 | 137.8 | 18,500 |
| 101 | 137.6 | 18,589 | 141.5 | 19,117 | 138.2 | 18,460 | 142.1 | 18,982 | 133.3 | 17,902 | 138.7 | 18,628 | 133.9 | 17,781 | 139.3 | 18,500 |
| 102 | 138.9 | 18,565 | 143.0 | 19,116 | 139.5 | 18,437 | 143.6 | 18,982 | 134.5 | 17,879 | 140.1 | 18,627 | 135.1 | 17,759 | 140.7 | 18,499 |
| 103 | 140.2 | 18,542 | 144.5 | 19,115 | 140.8 | 18,414 | 145.1 | 18,981 | 135.7 | 17,857 | 141.6 | 18,626 | 136.3 | 17,737 | 142.2 | 18,498 |
| 104 | 141.4 | 18,519 | 146.0 | 19,113 | 142.0 | 18,391 | 146.6 | 18,979 | 137.0 | 17,835 | 143.1 | 18,625 | 137.6 | 17,716 | 143.7 | 18,497 |
| 105 | 142.7 | 18,496 | 147.5 | 19,112 | 143.3 | 18,369 | 148.1 | 18,978 | 138.2 | 17,813 | 144.5 | 18,624 | 138.8 | 17,694 | 145.1 | 18,496 |
| 106 | 143.6 | 18,422 | 148.8 | 19,094 | 144.2 | 18,295 | 149.5 | 18,960 | 139.1 | 17,741 | 145.8 | 18,606 | 139.7 | 17,623 | 146.5 | 18,479 |
| 107 | 144.5 | 18,348 | 150.2 | 19,076 | 145.1 | 18,222 | 150.8 | 18,942 | 139.9 | 17,670 | 147.2 | 18,588 | 140.5 | 17,552 | 147.8 | 18,461 |
| 108 | 145.3 | 18,276 | 151.6 | 19,058 | 146.0 | 18,150 | 152.2 | 18,925 | 140.8 | 17,601 | 148.5 | 18,571 | 141.4 | 17,484 | 149.2 | 18,444 |
| 109 | 146.2 | 18,205 | 152.9 | 19,040 | 146.8 | 18,080 | 153.6 | 18,907 | 141.6 | 17,532 | 149.9 | 18,554 | 142.2 | 17,416 | 150.5 | 18,427 |
| 110 | 147.1 | 18,135 | 154.3 | 19,022 | 147.7 | 18,010 | 154.9 | 18,889 | 142.5 | 17,465 | 151.2 | 18,536 | 143.1 | 17,349 | 151.8 | 18,410 |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **Project Head (feet)** | **Unit 10 w/ Blades Hydraulically Locked at 29° (*PRELIM as of Nov 2020*)** | | | | | | | | **Unit 11 w/ Blades Welded at 29.9° (April 2012)** | | | | | | | |
| **With STS** | | | | **No STS** | | | | **With STS** | | | | **No STS** | | | |
| **Lower Limit** | | **Upper Limit** | | **Lower Limit** | | **Upper Limit** | | **Lower Limit** | | **Upper Limit** | | **Lower Limit** | | **Upper Limit** | |
| **MW** | **cfs** | **MW** | **cfs** | **MW** | **cfs** | **MW** | **cfs** | **MW** | **cfs** | **MW** | **cfs** | **MW** | **cfs** | **MW** | **cfs** |
| 80 | 101.9 | 17,719 | 107.5 | 18,686 | 102.4 | 17,595 | 107.9 | 18,552 | 106.1 | 18,487 | 111.2 | 19,368 | 106.6 | 18,354 | 111.6 | 19,226 |
| 81 | 103.3 | 17,704 | 108.7 | 18,640 | 103.7 | 17,581 | 109.2 | 18,507 | 107.4 | 18,451 | 112.4 | 19,307 | 107.9 | 18,319 | 112.9 | 19,166 |
| 82 | 104.6 | 17,689 | 110.0 | 18,594 | 105.1 | 17,567 | 110.5 | 18,462 | 108.7 | 18,416 | 113.6 | 19,246 | 109.2 | 18,285 | 114.1 | 19,106 |
| 83 | 106.0 | 17,674 | 111.3 | 18,549 | 106.5 | 17,552 | 111.7 | 18,417 | 110.1 | 18,381 | 114.9 | 19,187 | 110.5 | 18,251 | 115.4 | 19,047 |
| 84 | 107.4 | 17,659 | 112.5 | 18,504 | 107.9 | 17,537 | 113.0 | 18,373 | 111.4 | 18,346 | 116.1 | 19,128 | 111.9 | 18,216 | 116.6 | 18,990 |
| 85 | 108.8 | 17,643 | 113.8 | 18,460 | 109.2 | 17,522 | 114.3 | 18,329 | 112.7 | 18,312 | 117.4 | 19,070 | 113.2 | 18,182 | 117.9 | 18,932 |
| 86 | 110.4 | 17,678 | 115.3 | 18,466 | 110.9 | 17,557 | 115.8 | 18,335 | 114.4 | 18,348 | 118.9 | 19,071 | 114.9 | 18,219 | 119.4 | 18,933 |
| 87 | 112.1 | 17,711 | 117.0 | 18,489 | 112.6 | 17,590 | 117.5 | 18,358 | 116.1 | 18,383 | 120.6 | 19,096 | 116.6 | 18,253 | 121.1 | 18,959 |
| 88 | 113.7 | 17,743 | 118.6 | 18,510 | 114.2 | 17,621 | 119.1 | 18,380 | 117.8 | 18,416 | 122.3 | 19,120 | 118.3 | 18,287 | 122.8 | 18,983 |
| 89 | 115.4 | 17,773 | 120.3 | 18,531 | 115.9 | 17,652 | 120.8 | 18,401 | 119.5 | 18,448 | 124.0 | 19,143 | 120.1 | 18,319 | 124.6 | 19,006 |
| 90 | 117.0 | 17,802 | 121.5 | 18,481 | 117.5 | 17,681 | 122.0 | 18,351 | 121.2 | 18,478 | 125.1 | 19,067 | 121.8 | 18,349 | 125.6 | 18,931 |
| 91 | 118.4 | 17,800 | 123.1 | 18,509 | 119.0 | 17,679 | 123.7 | 18,379 | 122.7 | 18,479 | 126.8 | 19,097 | 123.3 | 18,350 | 127.4 | 18,961 |
| 92 | 119.9 | 17,797 | 124.8 | 18,535 | 120.4 | 17,676 | 125.4 | 18,406 | 124.2 | 18,479 | 128.6 | 19,125 | 124.8 | 18,350 | 129.1 | 18,989 |
| 93 | 121.3 | 17,793 | 126.5 | 18,561 | 121.8 | 17,673 | 127.0 | 18,432 | 125.7 | 18,479 | 130.3 | 19,153 | 126.3 | 18,350 | 130.8 | 19,017 |
| 94 | 122.7 | 17,790 | 128.2 | 18,586 | 123.2 | 17,670 | 128.7 | 18,457 | 127.2 | 18,478 | 132.0 | 19,179 | 127.8 | 18,350 | 132.6 | 19,043 |
| 95 | 124.1 | 17,786 | 129.9 | 18,609 | 124.7 | 17,666 | 130.4 | 18,480 | 128.7 | 18,477 | 133.8 | 19,205 | 129.3 | 18,349 | 134.3 | 19,069 |
| 96 | 125.6 | 17,799 | 131.4 | 18,623 | 126.2 | 17,679 | 132.0 | 18,494 | 130.3 | 18,485 | 135.4 | 19,211 | 130.8 | 18,358 | 135.9 | 19,075 |
| 97 | 127.1 | 17,812 | 133.0 | 18,636 | 127.7 | 17,692 | 133.5 | 18,507 | 131.8 | 18,493 | 137.0 | 19,217 | 132.4 | 18,365 | 137.5 | 19,081 |
| 98 | 128.6 | 17,825 | 134.5 | 18,648 | 129.1 | 17,705 | 135.1 | 18,519 | 133.4 | 18,500 | 138.6 | 19,222 | 134.0 | 18,373 | 139.2 | 19,087 |
| 99 | 130.1 | 17,836 | 136.1 | 18,660 | 130.6 | 17,717 | 136.6 | 18,531 | 134.9 | 18,506 | 140.2 | 19,227 | 135.5 | 18,379 | 140.8 | 19,092 |
| 100 | 131.5 | 17,848 | 137.6 | 18,671 | 132.1 | 17,728 | 138.2 | 18,542 | 136.5 | 18,512 | 141.8 | 19,231 | 137.1 | 18,385 | 142.4 | 19,096 |
| 101 | 132.8 | 17,825 | 139.0 | 18,665 | 133.4 | 17,705 | 139.6 | 18,537 | 137.8 | 18,490 | 143.4 | 19,246 | 138.4 | 18,364 | 144.0 | 19,111 |
| 102 | 134.0 | 17,802 | 140.5 | 18,659 | 134.6 | 17,683 | 141.1 | 18,531 | 139.0 | 18,469 | 145.0 | 19,260 | 139.6 | 18,342 | 145.6 | 19,125 |
| 103 | 135.3 | 17,779 | 141.9 | 18,653 | 135.9 | 17,660 | 142.5 | 18,525 | 140.3 | 18,447 | 146.6 | 19,273 | 140.9 | 18,321 | 147.2 | 19,138 |
| 104 | 136.5 | 17,756 | 143.4 | 18,647 | 137.1 | 17,638 | 144.0 | 18,519 | 141.6 | 18,426 | 148.2 | 19,287 | 142.2 | 18,300 | 148.8 | 19,152 |
| 105 | 137.8 | 17,734 | 144.8 | 18,641 | 138.4 | 17,616 | 145.4 | 18,513 | 142.8 | 18,405 | 149.8 | 19,299 | 143.4 | 18,279 | 150.4 | 19,164 |
| 106 | 138.6 | 17,666 | 146.1 | 18,626 | 139.2 | 17,549 | 146.8 | 18,498 | 143.6 | 18,327 | 151.1 | 19,283 | 144.2 | 18,201 | 151.7 | 19,148 |
| 107 | 139.5 | 17,600 | 147.5 | 18,611 | 140.1 | 17,483 | 148.1 | 18,483 | 144.4 | 18,249 | 152.5 | 19,267 | 145.1 | 18,125 | 153.1 | 19,132 |
| 108 | 140.3 | 17,535 | 148.8 | 18,595 | 141.0 | 17,418 | 149.5 | 18,468 | 145.2 | 18,173 | 153.9 | 19,251 | 145.9 | 18,049 | 154.5 | 19,116 |
| 109 | 141.2 | 17,471 | 150.2 | 18,580 | 141.8 | 17,355 | 150.8 | 18,453 | 146.1 | 18,099 | 155.2 | 19,235 | 146.7 | 17,975 | 155.3 | 19,032 |
| 110 | 142.1 | 17,408 | 151.5 | 18,565 | 142.7 | 17,292 | 152.2 | 18,439 | 146.9 | 18,025 | 155.3 | 19,061 | 147.5 | 17,903 | 155.3 | 18,850 |

|  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **Project Head (feet)** | **Unit 14 w/ Blades Welded at 29.6° (Aug 2019)** | | | | | | | |
| **With STS** | | | | **No STS** | | | |
| **Lower Limit** | | **Upper Limit** | | **Lower Limit** | | **Upper Limit** | |
| **MW** | **cfs** | **MW** | **cfs** | **MW** | **cfs** | **MW** | **cfs** |
| 80 | 106.5 | 18,639 | 110.6 | 19,356 | 106.9 | 18,501 | 111.0 | 19,210 |
| 81 | 107.9 | 18,617 | 111.9 | 19,304 | 108.3 | 18,479 | 112.3 | 19,158 |
| 82 | 109.3 | 18,596 | 113.2 | 19,252 | 109.7 | 18,458 | 113.6 | 19,107 |
| 83 | 110.7 | 18,573 | 114.4 | 19,200 | 111.2 | 18,436 | 114.9 | 19,056 |
| 84 | 112.1 | 18,551 | 115.7 | 19,149 | 112.6 | 18,415 | 116.2 | 19,006 |
| 85 | 113.5 | 18,528 | 117.0 | 19,099 | 114.0 | 18,393 | 117.5 | 18,956 |
| 86 | 115.2 | 18,565 | 118.6 | 19,104 | 115.7 | 18,430 | 119.0 | 18,961 |
| 87 | 117.0 | 18,601 | 120.3 | 19,132 | 117.4 | 18,465 | 120.8 | 18,990 |
| 88 | 118.7 | 18,634 | 122.0 | 19,159 | 119.2 | 18,499 | 122.5 | 19,017 |
| 89 | 120.4 | 18,667 | 123.7 | 19,185 | 120.9 | 18,531 | 124.2 | 19,043 |
| 90 | 122.1 | 18,698 | 124.9 | 19,116 | 122.6 | 18,562 | 125.4 | 18,975 |
| 91 | 123.6 | 18,697 | 126.6 | 19,146 | 124.1 | 18,561 | 127.1 | 19,005 |
| 92 | 125.1 | 18,695 | 128.3 | 19,174 | 125.6 | 18,560 | 128.8 | 19,033 |
| 93 | 126.6 | 18,692 | 130.0 | 19,202 | 127.1 | 18,558 | 130.6 | 19,060 |
| 94 | 128.1 | 18,690 | 131.8 | 19,228 | 128.6 | 18,555 | 132.3 | 19,087 |
| 95 | 129.6 | 18,687 | 133.5 | 19,253 | 130.1 | 18,553 | 134.0 | 19,112 |
| 96 | 131.1 | 18,701 | 135.1 | 19,267 | 131.7 | 18,567 | 135.6 | 19,126 |
| 97 | 132.7 | 18,715 | 136.7 | 19,280 | 133.2 | 18,581 | 137.2 | 19,139 |
| 98 | 134.2 | 18,728 | 138.3 | 19,292 | 134.8 | 18,594 | 138.8 | 19,151 |
| 99 | 135.8 | 18,741 | 139.9 | 19,304 | 136.3 | 18,607 | 140.4 | 19,164 |
| 100 | 137.3 | 18,753 | 141.5 | 19,316 | 137.9 | 18,619 | 142.0 | 19,175 |
| 101 | 138.6 | 18,729 | 143.0 | 19,315 | 139.2 | 18,596 | 143.5 | 19,175 |
| 102 | 139.9 | 18,706 | 144.5 | 19,314 | 140.5 | 18,572 | 145.1 | 19,174 |
| 103 | 141.2 | 18,682 | 146.0 | 19,313 | 141.8 | 18,549 | 146.6 | 19,173 |
| 104 | 142.5 | 18,659 | 147.5 | 19,312 | 143.1 | 18,526 | 148.1 | 19,172 |
| 105 | 143.8 | 18,636 | 149.0 | 19,310 | 144.4 | 18,504 | 149.6 | 19,170 |
| 106 | 144.7 | 18,561 | 150.3 | 19,277 | 145.3 | 18,429 | 150.7 | 19,122 |
| 107 | 145.6 | 18,487 | 151.5 | 19,244 | 146.2 | 18,356 | 151.9 | 19,074 |
| 108 | 146.4 | 18,414 | 152.8 | 19,211 | 147.0 | 18,284 | 153.0 | 19,027 |
| 109 | 147.3 | 18,343 | 154.0 | 19,179 | 147.9 | 18,213 | 154.2 | 18,980 |
| 110 | 148.2 | 18,272 | 155.3 | 19,147 | 148.8 | 18,143 | 155.3 | 18,934 |

**a.** Units 3, 4, 8, 9, 10, 11, and 14 have runner blades that are locked at a fixed angle (non-adjustable) and a restricted operating range until the unit is repaired.

1. Dewatering Plans
   1. General
      1. *Guidelines for Dewatering and Fish Handling* (**Appendix F**) and project *Dewatering Plans*[[5]](#footnote-5) have been developed by the projects and approved by FPOM, and are followed for most project facility dewaterings. The appropriate plans are reviewed by participants before each salvage operation. The plans include consideration for fish safety and are consistent with the following general guidance.
      2. The Project biologist and/or alternate Corps fish personnel will attend all project activities involving fish handling. Personnel shall remain present onsite during pumping operations to ensure stranding does not occur or a water level sensor that deactivates the dewatering process will be used. During the pumping or draining operation to dewater a portion or all, the water level will not be allowed to drop so low it strands fish. The fish agencies and tribes will be encouraged to participate in all ladder dewaterings.
   2. Dewatering – Adult Fish Ladders
      1. When possible prior to dewatering, operate ladders to be dewatered at orifice flow, with the AWS off, for at least 24 hours but not more than 96 hours. For non-routine or unscheduled maintenance, discontinue auxiliary water and operate ladder at reduced flow as long as possible for up to 72 hours prior to dewatering and follow guidance in **section** **6.4**.
      2. Project personnel will install head gates[[6]](#footnote-6) to shut down ladder flow. Where possible, a flushing flow of 1”–2" will be maintained in the ladder until fish are rescued.
      3. A Project biologist will ensure availability of fish rescue equipment and adequate numbers of personnel necessary to move fish out of the dewatered ladder. The Project Biologist or alternate Corps fish personnel will oversee fish rescue when the ladders are dewatered. The Project Biologist will invite fish agency and/or tribal biologists to participate in the dewatering activities. Juvenile fish will be transported and released in the tailrace and adults released in the forebay (except identifiable steelhead kelts should be released into the tailrace).
      4. Orifice blocking devices, which are placed in the lower-most weirs to prevent fish from re-ascending the dewatered portion of the adult fishway, shall have ropes attached to them by project operations and be tied off to fishway railings. The blocking devices shall be removed just before the fishway is returned to service. These devices will be noted on the pre-water-up checklist maintained by Project fish biologists. This will prevent the orifice blocks from being unintentionally left in place following fishway water-up.
   3. Dewatering – Powerhouse Fish Collection System
      1. During the pumping or draining operation to dewater a portion or the entire collection channel, the water will not be allowed to drop to a level which strands fish. Personnel shall remain present onsite during pumping operations to ensure that stranding does not occur. The Project Biologist will assure that all necessary rescue equipment is available. The Project Biologist or alternate Corps fish personnel will provide technical guidance on fish safety and will assist directly in rescue operations.
   4. Dewatering – Juvenile Bypass System (JBS)
      1. When draining the juvenile bypass channel, it is typical to flush the channel with only Unit 16 bypass orifices open. Unit 16 gatewells will be dipped in advance to minimize the number of fish contained in this flushing water during fish passage season.
   5. Dewatering – Turbine Units
      1. **Gatewell Dipping:** Remove juvenile fish from gatewell(s) that will be drained by use of a special dipping basket. During fish passage season, April 1–December 15, gatewell dipping is mandatory whether or not fish screens are installed. Dipping is not required during winter maintenance, December 16–March 31, when fish screens have been removed. To minimize the number of fish contained in the gatewell:

Shut down the turbine the previous evening/night and leave idle with all orifices open overnight if power demand allows;

Keep orifices open during the removal of screens/STSs, during turbine spinning, and while gatewell dipping is performed;

Close orifices only after gatewell dipping/fish removal has been completed and immediately before installing the bulkhead;

It is strongly preferred that, if possible, two roller gates and one bulkhead are deployed to isolate a turbine for dewatering.

* + 1. If the turbine draft tube is dewatered, operate unit at full load for a minimum of 15 minutes immediately prior to installing tail logs. If not possible to load, run unit at speed-no-load for a minimum of 15 minutes. Install the bottom two tail logs side-by-side prior to stacking the remainder to minimize risk of sturgeon entering the draft tube before dewatering. This is necessary for both scheduled and unscheduled outages.
    2. If a turbine unit is idle and partially dewatered, and tail logs are to be put into place, an adequate safety pool may be maintained for up to 4 days to accommodate fish trapped in the draft tube. If longer timeframes are needed for the safety pool, project fisheries will coordinate with FPOM on a case-by-case basis. Adequate inspections will need to be conducted to ensure that the safety pool is maintained and fish are in good condition. Water levels in the draft tube will not be allowed to drop to a level that strands fish.
    3. Fish rescue personnel will inspect dewatered turbine draft tubes, scroll cases, and intakes as soon as they can gain access and the water levels reach a depth permitting visual inspection. The Project Biologist or alternate fish personnel will provide technical guidance on fish safety and will directly participate in fish salvage. The Project Biologist will ensure that all necessary rescue equipment is available.
  1. Dewatering – Navigation Lock
     1. The navigation lock is frequently dewatered for routine maintenance in late February/early March, in conjunction with navigation lock outages at The Dalles and Bonneville dams. The area between the upstream bulkhead and the upstream gate is surveyed for fish as water levels allow. The lateral and pool areas on the floor of the lock are surveyed for fish from above. Most of these areas remain full of water, precluding the ability to implement successful fish salvage operations. Areas where water levels slowly decrease are accessed via crane when pool levels reach a depth of approximately 3 feet. The fill conduits are accessed and checked for fish only if needed and can be done safely. All salvaged fish are removed, transported via bag or tank and released to the river.

1. Forebay Debris Removal

Debris at projects can impact fish passage conditions by plugging or blocking trash racks, VBSs, gatewell orifices, dewatering screens, separators, and facility piping resulting in impingement, injuries, and descaling of fish. Removing debris at its source in the forebay is sometimes necessary to maintain safe and efficient fish passage conditions, navigation, and other project activities. In this case, the only viable alternative is to spill to pass the debris.Special spill operations that don’t follow the normal spill schedule or volume limits will be coordinated prior to their execution. Normally, the project shall contact CENWP-OD at least two workdays prior to the day the special operation is required. Using information provided by the project, CENWP-OD will coordinate with FPOM and with RCC, as necessary. Once the coordination is complete, RCC will issue a teletype detailing the special operations.

1. Response to Hazardous Materials Spills

John Day Project’s guidance for responding to hazardous substance spills is contained in its *Emergency Spill Response Plan*. This guidance will be followed in case of a spill. In the event of a hazardous materials spill, the Project Biologist has the authority to make fishway adjustments outside of operating criteria as necessary to prevent contamination of the ladder until unified command is formed and consultation is established with FPOM. NOAA Fisheries will be notified within 24 hours of a ladder closure.

Project Fisheries will be contacted as soon as possible after a hazardous material release and prior to any modification to fishway operations. Project Fisheries will then contact the CENWP-OD biologist and FPOM. Attempts should be made to first contact the Project Biologist on duty. During fish passage season there is a Project Biologist on duty 7 days/week. If a Project Biologist cannot be reached by radio or in the office, attempts to contact Project Fisheries will occur in the following order (contact info available in the Control Room): Eric Grosvenor; Michael Lotspeich; Tammy Mackey.

Table JDA-8. [*pg 1 of 11*] John Day Dam Spill Patterns with TSWs in Bays 18-19.

| **JDA Spill Patterns with TSWs in Bays 18, 19 - # Gate Stops per Spillbay** | | | | | | | | | | | | | | | | | | | | **Total** | **Spill** [[7]](#footnote-7) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **1[[8]](#footnote-8)** | **2** | **3** | **4** | **5** | **6** | **7** | **8** | **9** | **10** | **11** | **12** | **13** | **14** | **15** | **16** | **17** | **18 [[9]](#footnote-9)** | **19 c** | **20 b** | **Stops (#)** | **(kcfs)** |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | TSW | TSW |  | **0** | **19.4** |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | TSW | TSW | 1 | **1** | **21** |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | TSW | TSW | 1.5 | **1.5** | **21.8** |
|  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | TSW | TSW | 1.5 | **2.5** | **23.4** |
|  | 1 | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  | TSW | TSW | 1.5 | **3.5** | **25** |
|  | 1 | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  | 1 | TSW | TSW | 1.5 | **4.5** | **26.6** |
|  | 1 | 1 |  |  |  |  |  |  |  |  |  |  |  |  | 1 | 1 | TSW | TSW | 1.5 | **5.5** | **28.2** |
|  | 1 | 1 |  |  |  |  |  |  |  |  |  |  |  | 1 | 1 | 1 | TSW | TSW | 1.5 | **6.5** | **29.8** |
|  | 1 | 1 |  |  |  |  |  |  |  |  |  |  | 1 | 1 | 1 | 1 | TSW | TSW | 1.5 | **7.5** | **31.4** |
|  | 1 | 1 |  |  |  |  |  |  |  |  |  | 1 | 1 | 1 | 1 | 1 | TSW | TSW | 1.5 | **8.5** | **33** |
|  | 1 | 1 |  |  |  |  |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | TSW | TSW | 1.5 | **9.5** | **34.6** |
|  | 1 | 1 |  |  |  |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | TSW | TSW | 1.5 | **10.5** | **36.2** |
|  | 1 | 1 |  |  |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | TSW | TSW | 1.5 | **11.5** | **37.8** |
|  | 1 | 1 |  |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | TSW | TSW | 1.5 | **12.5** | **39.4** |
|  | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | TSW | TSW | 1.5 | **13.5** | **41** |
|  | 1 | 1 |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | TSW | TSW | 1.5 | **14.5** | **42.6** |
|  | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | TSW | TSW | 1.5 | **15.5** | **44.2** |
|  | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.5 | TSW | TSW | 1.5 | **16** | **45** |
|  | 2 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.5 | TSW | TSW | 1.5 | **16.5** | **45.8** |
|  | 2 | 1.5 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.5 | TSW | TSW | 1.5 | **17** | **46.6** |
|  | 2 | 1.5 | 1 | 1 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.5 | TSW | TSW | 1.5 | **18** | **48.2** |
|  | 2 | 1.5 | 1 | 1 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.5 | 1.5 | TSW | TSW | 1.5 | **18.5** | **49** |
|  | 2 | 1.5 | 1.5 | 1 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.5 | 1.5 | TSW | TSW | 1.5 | **19** | **49.8** |
|  | 2 | 1.5 | 1.5 | 1 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.5 | 1.5 | TSW | TSW | 2 | **19.5** | **50.6** |
|  | 2 | 1.5 | 1.5 | 1 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.5 | 2 | TSW | TSW | 2 | **20** | **51.4** |
|  | 2 | 1.5 | 1.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.5 | 2 | TSW | TSW | 2 | **21** | **53** |
|  | 2 | 1.5 | 1.5 | 1.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.5 | 2 | TSW | TSW | 2 | **21.5** | **53.8** |
|  | 2 | 1.5 | 1 | 1.5 | 1 | 1 | 1 | 1.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1.5 | 2 | TSW | TSW | 2 | **22** | **54.6** |
|  | 2 | 1.5 | 1 | 1.5 | 1 | 1.5 | 1 | 1.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1.5 | 2 | TSW | TSW | 2 | **22.5** | **55.4** |
|  | 2 | 1.5 | 1 | 1.5 | 1 | 1.5 | 1 | 1.5 | 1 | 1 | 1 | 1 | 1 | 1.5 | 1.5 | 2 | TSW | TSW | 2 | **23** | **56.2** |
|  | 2 | 1.5 | 1 | 1.5 | 1 | 1.5 | 1 | 1.5 | 1 | 1 | 1 | 1 | 1 | 1.5 | 2 | 2 | TSW | TSW | 2 | **23.5** | **57** |
|  | 3 | 1.5 | 1 | 1.5 | 1 | 1.5 | 1 | 1.5 | 1 | 1 | 1 | 1 | 1 | 1.5 | 2 | 2 | TSW | TSW | 2 | **24** | **57.8** |
|  | 3 | 1.5 | 1 | 1.5 | 1 | 1.5 | 1 | 1.5 | 1.5 | 1 | 1 | 1 | 1 | 1.5 | 2 | 2 | TSW | TSW | 2 | **24.5** | **58.6** |
|  | 3 | 1.5 | 1 | 1.5 | 1 | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 1 | 1 | 1 | 1.5 | 2 | 2 | TSW | TSW | 2 | **25** | **59.4** |
|  | 3 | 1.5 | 1 | 1.5 | 1 | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 1 | 1 | 1.5 | 1.5 | 2 | 2 | TSW | TSW | 2 | **25.5** | **60.2** |
|  | 3 | 1.5 | 1 | 1.5 | 1 | 1.5 | 1.5 | 2 | 1.5 | 1 | 1 | 1 | 1.5 | 1.5 | 2 | 2 | TSW | TSW | 2 | **26** | **61** |
|  | 3 | 1.5 | 1 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 1.5 | 1 | 1 | 1 | 1.5 | 1.5 | 2 | 2 | TSW | TSW | 2 | **26.5** | **61.8** |
|  | 3 | 1.5 | 1 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 1.5 | 1 | 1 | 1.5 | 1.5 | 1.5 | 2 | 2 | TSW | TSW | 2 | **27** | **62.6** |
|  | 3 | 1.5 | 1 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 1.5 | 1 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2 | TSW | TSW | 2 | **27.5** | **63.4** |
|  | 3 | 1.5 | 1 | 1.5 | 1.5 | 2 | 1.5 | 2 | 1.5 | 1 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2 | TSW | TSW | 2 | **28** | **64.2** |
|  | 3 | 1.5 | 1 | 1.5 | 1.5 | 2 | 1.5 | 2 | 1.5 | 1 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2.5 | TSW | TSW | 2 | **28.5** | **65** |
|  | 3 | 1.5 | 1 | 1.5 | 1.5 | 2 | 1.5 | 2 | 1.5 | 1 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2.5 | TSW | TSW | 2 | **29** | **65.8** |
|  | 3 | 1.5 | 1 | 1.5 | 1.5 | 2 | 1.5 | 2 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2.5 | TSW | TSW | 2 | **29.5** | **66.6** |
|  | 3 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 1.5 | 2 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2.5 | TSW | TSW | 2 | **30** | **67.4** |
|  | 3 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2.5 | TSW | TSW | 2 | **30.5** | **68.2** |
|  | 3 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2 | 2.5 | TSW | TSW | 2 | **31** | **69** |
|  | 3 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2.5 | 2.5 | TSW | TSW | 2 | **31.5** | **69.8** |
|  | 3 | 2 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2.5 | 2.5 | TSW | TSW | 2 | **32** | **70.6** |
|  | 3 | 2 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2 | 1.5 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2.5 | 2.5 | TSW | TSW | 2.5 | **32.5** | **71.4** |
|  | 3 | 2 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2 | 2.5 | 2.5 | TSW | TSW | 2.5 | **33** | **72.2** |
|  | 3 | 2 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2 | 2.5 | 2.5 | TSW | TSW | 2.5 | **33.5** | **73** |
|  | 3 | 2 | 1.5 | 2 | 1.5 | 2 | 2 | 2 | 1.5 | 1.5 | 1.5 | 2 | 2 | 2 | 2.5 | 2.5 | TSW | TSW | 2.5 | **34** | **73.8** |
|  | 3 | 2 | 1.5 | 2 | 1.5 | 2 | 2 | 2 | 1.5 | 1.5 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | TSW | TSW | 2.5 | **34.5** | **74.6** |
|  | 3 | 2 | 1.5 | 2 | 1.5 | 2 | 2 | 2 | 2 | 1.5 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | TSW | TSW | 2.5 | **35** | **75.4** |
|  | 3 | 2 | 1.5 | 2 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | TSW | TSW | 2.5 | **35.5** | **76.2** |
|  | 3 | 2 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | TSW | TSW | 2.5 | **36** | **77** |
|  | 3 | 2 | 1.5 | 2 | 2 | 2.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | TSW | TSW | 2.5 | **36.5** | **77.8** |
|  | 3 | 2 | 2 | 2 | 2 | 2.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | TSW | TSW | 2.5 | **37** | **78.6** |
|  | 3 | 2.5 | 2 | 2 | 2 | 2.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | TSW | TSW | 2.5 | **37.5** | **79.4** |
|  | 3 | 2.5 | 2 | 2 | 2.5 | 2.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | TSW | TSW | 2.5 | **38** | **80.2** |
|  | 4 | 2.5 | 2 | 2 | 2.5 | 2.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | TSW | TSW | 2.5 | **38.5** | **81** |
|  | 4 | 2.5 | 2 | 2 | 2.5 | 2.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | 2.5 | TSW | TSW | 2.5 | **39** | **81.8** |
|  | 4 | 2.5 | 2 | 2 | 2.5 | 2.5 | 2.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | 2.5 | TSW | TSW | 2.5 | **39.5** | **82.6** |
|  | 4 | 2.5 | 2 | 2 | 2.5 | 2.5 | 2.5 | 2 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | TSW | TSW | 2.5 | **40** | **83.4** |
|  | 4 | 2.5 | 1.5 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2 | 2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | TSW | TSW | 2.5 | **40.5** | **84.2** |
|  | 4 | 2.5 | 1.5 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | TSW | TSW | 2.5 | **41** | **85** |
|  | 4 | 2.5 | 1.5 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2 | 2 | 2.5 | 2.5 | 2.5 | 3 | 2.5 | TSW | TSW | 2.5 | **41.5** | **85.8** |
|  | 4 | 2.5 | 1.5 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2 | 2 | 2.5 | 2.5 | 3 | 3 | 2.5 | TSW | TSW | 2.5 | **42** | **86.6** |
|  | 4 | 2.5 | 1.5 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2 | 2.5 | 2.5 | 2.5 | 3 | 3 | 2.5 | TSW | TSW | 2.5 | **42.5** | **87.4** |
|  | 4 | 3 | 1.5 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2 | 2.5 | 2.5 | 2.5 | 3 | 3 | 2.5 | TSW | TSW | 2.5 | **43** | **88.2** |
|  | 4 | 3 | 1.5 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2 | 2.5 | 2.5 | 3 | 3 | 3 | 2.5 | TSW | TSW | 2.5 | **43.5** | **89** |
|  | 4 | 3 | 1.5 | 2 | 2.5 | 3 | 2.5 | 2.5 | 2.5 | 2 | 2.5 | 2.5 | 3 | 3 | 3 | 2.5 | TSW | TSW | 2.5 | **44** | **89.8** |
|  | 4 | 3 | 1.5 | 2 | 2.5 | 3 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 3 | 3 | 3 | 2.5 | TSW | TSW | 2.5 | **44.5** | **90.6** |
|  | 4 | 3 | 2 | 2 | 2.5 | 3 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 3 | 3 | 3 | 2.5 | TSW | TSW | 2.5 | **45** | **91.4** |
|  | 4 | 3 | 2 | 2 | 2.5 | 3 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 3 | 3 | 3 | 3 | TSW | TSW | 2.5 | **45.5** | **92.2** |
|  | 4 | 3 | 2 | 2.5 | 2.5 | 3 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 3 | 3 | 3 | 3 | TSW | TSW | 2.5 | **46** | **93** |
|  | 4 | 3 | 2 | 2.5 | 2.5 | 3 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 3 | 3 | 3.5 | 3 | TSW | TSW | 2.5 | **46.5** | **93.8** |
|  | 4 | 3.5 | 2 | 2.5 | 2.5 | 3 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 3 | 3 | 3.5 | 3 | TSW | TSW | 2.5 | **47** | **94.6** |
|  | 4 | 3.5 | 2 | 2.5 | 2.5 | 3 | 3 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 3 | 3 | 3.5 | 3 | TSW | TSW | 2.5 | **47.5** | **95.4** |
|  | 4 | 3.5 | 2 | 2.5 | 2.5 | 3 | 3 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 3 | 3 | 3.5 | 3.5 | TSW | TSW | 2.5 | **48** | **96.2** |
|  | 4 | 3.5 | 2 | 3 | 2.5 | 3 | 3 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 3 | 3 | 3.5 | 3.5 | TSW | TSW | 2.5 | **48.5** | **97** |
|  | 4 | 3.5 | 2.5 | 3 | 2.5 | 3 | 3 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 3 | 3 | 3.5 | 3.5 | TSW | TSW | 2.5 | **49** | **97.8** |
|  | 4 | 3.5 | 2.5 | 3 | 2.5 | 3 | 3 | 2.5 | 2.5 | 2.5 | 3 | 2.5 | 3 | 3 | 3.5 | 3.5 | TSW | TSW | 2.5 | **49.5** | **98.6** |
|  | 4 | 3.5 | 2.5 | 3 | 2.5 | 3 | 3 | 3 | 2.5 | 2.5 | 3 | 2.5 | 3 | 3 | 3.5 | 3.5 | TSW | TSW | 2.5 | **50** | **99.4** |
|  | 4 | 3.5 | 2.5 | 3 | 2.5 | 3 | 3 | 3 | 3 | 2.5 | 3 | 2.5 | 3 | 3 | 3.5 | 3.5 | TSW | TSW | 2.5 | **50.5** | **100.2** |
|  | 4 | 3.5 | 2.5 | 3 | 2.5 | 3 | 3 | 3 | 3 | 2.5 | 3 | 3 | 3 | 3 | 3.5 | 3.5 | TSW | TSW | 2.5 | **51** | **101** |
|  | 4 | 3.5 | 2.5 | 3.5 | 2.5 | 3 | 3 | 3 | 3 | 2.5 | 3 | 3 | 3 | 3 | 3.5 | 3.5 | TSW | TSW | 2.5 | **51.5** | **101.8** |
|  | 4 | 3.5 | 3 | 3.5 | 2.5 | 3 | 3 | 3 | 3 | 2.5 | 3 | 3 | 3 | 3 | 3.5 | 3.5 | TSW | TSW | 2.5 | **52** | **102.6** |
|  | 4 | 3.5 | 3 | 3.5 | 2.5 | 3 | 3 | 3 | 3 | 2.5 | 3 | 3 | 3 | 3 | 3.5 | 4 | TSW | TSW | 2.5 | **52.5** | **103.4** |
|  | 4 | 3.5 | 3 | 3.5 | 2.5 | 3 | 3 | 3 | 3 | 2.5 | 3 | 3 | 3 | 3.5 | 3.5 | 4 | TSW | TSW | 2.5 | **53** | **104.2** |
|  | 4 | 3.5 | 3 | 3.5 | 2.5 | 3 | 3 | 3 | 3 | 2.5 | 3 | 3 | 3 | 3.5 | 3.5 | 4 | TSW | TSW | 2.5 | **53.5** | **105** |
|  | 4 | 3.5 | 3 | 3.5 | 2.5 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3.5 | 3.5 | 4 | TSW | TSW | 2.5 | **54** | **105.8** |
|  | 4 | 3.5 | 3 | 3.5 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3.5 | 3.5 | 4 | TSW | TSW | 2.5 | **54.5** | **106.6** |
|  | 4 | 3.5 | 3 | 3.5 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3.5 | 4 | 4 | TSW | TSW | 2.5 | **55** | **107.4** |
|  | 4 | 3.5 | 3 | 3.5 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3.5 | 3.5 | 4 | 4 | TSW | TSW | 2.5 | **55.5** | **108.2** |
|  | 4 | 4 | 3 | 3.5 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3.5 | 3.5 | 4 | 4 | TSW | TSW | 2.5 | **56** | **109** |
|  | 4 | 4 | 3 | 3.5 | 3 | 3 | 3 | 3 | 3 | 3 | 3.5 | 3 | 3.5 | 3.5 | 4 | 4 | TSW | TSW | 2.5 | **56.5** | **109.8** |
|  | 4 | 4 | 3 | 3.5 | 3 | 3.5 | 3 | 3 | 3 | 3 | 3.5 | 3 | 3.5 | 3.5 | 4 | 4 | TSW | TSW | 2.5 | **57** | **110.6** |
|  | 4 | 4 | 3 | 3.5 | 3 | 3.5 | 3 | 3 | 3 | 3.5 | 3.5 | 3 | 3.5 | 3.5 | 4 | 4 | TSW | TSW | 2.5 | **57.5** | **111.4** |
|  | 4 | 4 | 3 | 3.5 | 3 | 3.5 | 3 | 3 | 3 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4 | TSW | TSW | 2.5 | **58** | **112.2** |
|  | 4 | 4 | 3 | 3.5 | 3.5 | 3.5 | 3 | 3 | 3 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4 | TSW | TSW | 2.5 | **58.5** | **113** |
|  | 4 | 4 | 3 | 3.5 | 3.5 | 3.5 | 3 | 3.5 | 3 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4 | TSW | TSW | 2.5 | **59** | **113.8** |
|  | 4 | 4 | 3 | 3.5 | 3.5 | 3.5 | 3 | 3.5 | 3 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4.5 | TSW | TSW | 2.5 | **59.5** | **114.6** |
|  | 4 | 4 | 3 | 3.5 | 3.5 | 3.5 | 3 | 3.5 | 3 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4.5 | TSW | TSW | 3 | **60** | **115.4** |
|  | 4 | 4 | 3 | 3.5 | 3.5 | 3.5 | 3 | 3.5 | 3 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4 | 4.5 | TSW | TSW | 3 | **60.5** | **116.2** |
|  | 4 | 4 | 3.5 | 3.5 | 3.5 | 3.5 | 3 | 3.5 | 3 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4 | 4.5 | TSW | TSW | 3 | **61** | **117** |
|  | 4 | 4 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4 | 4.5 | TSW | TSW | 3 | **61.5** | **117.8** |
|  | 4 | 4 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4 | 4.5 | TSW | TSW | 3 | **62** | **118.6** |
|  | 4 | 4 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4.5 | 4.5 | TSW | TSW | 3 | **62.5** | **119.4** |
|  | 4 | 4 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4 | 4.5 | 4.5 | TSW | TSW | 3 | **63** | **120.2** |
|  | 4 | 4.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4 | 4.5 | 4.5 | TSW | TSW | 3 | **63.5** | **121** |
|  | 4 | 4.5 | 3.5 | 4 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4 | 4.5 | 4.5 | TSW | TSW | 3 | **64** | **121.8** |
|  | 4 | 4.5 | 3.5 | 4 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 3.5 | 4 | 4 | 4.5 | 4.5 | TSW | TSW | 3 | **64.5** | **122.6** |
|  | 4 | 4.5 | 3.5 | 4 | 3.5 | 4 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 3.5 | 4 | 4 | 4.5 | 4.5 | TSW | TSW | 3 | **65** | **123.4** |
|  | 4 | 4.5 | 3.5 | 4 | 3.5 | 4 | 3.5 | 3.5 | 3.5 | 4 | 4 | 3.5 | 4 | 4 | 4.5 | 4.5 | TSW | TSW | 3 | **65.5** | **124.2** |
|  | 4 | 4.5 | 3.5 | 4 | 3.5 | 4 | 3.5 | 3.5 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4.5 | 4.5 | TSW | TSW | 3 | **66** | **125** |
|  | 4 | 4.5 | 3.5 | 4 | 4 | 4 | 3.5 | 3.5 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4.5 | 4.5 | TSW | TSW | 3 | **66.5** | **125.8** |
|  | 4 | 4.5 | 3.5 | 4 | 4 | 4 | 3.5 | 4 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4.5 | 4.5 | TSW | TSW | 3 | **67** | **126.6** |
|  | 4 | 4.5 | 3.5 | 4 | 4 | 4 | 3.5 | 4 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4.5 | 5 | TSW | TSW | 3 | **67.5** | **127.4** |
|  | 4 | 4.5 | 3.5 | 4 | 4 | 4 | 3.5 | 4 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4.5 | 5 | TSW | TSW | 3.5 | **68** | **128.2** |
|  | 4 | 4.5 | 3.5 | 4 | 4 | 4 | 3.5 | 4 | 3.5 | 4 | 4 | 4 | 4 | 4.5 | 4.5 | 5 | TSW | TSW | 3.5 | **68.5** | **129** |
|  | 4 | 4.5 | 4 | 4 | 4 | 4 | 3.5 | 4 | 3.5 | 4 | 4 | 4 | 4 | 4.5 | 4.5 | 5 | TSW | TSW | 3.5 | **69** | **129.8** |
|  | 4 | 4.5 | 4 | 4 | 4 | 4 | 4 | 4 | 3.5 | 4 | 4 | 4 | 4 | 4.5 | 4.5 | 5 | TSW | TSW | 3.5 | **69.5** | **130.6** |
|  | 4 | 4.5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4.5 | 4.5 | 5 | TSW | TSW | 3.5 | **70** | **131.4** |
|  | 4 | 4.5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4.5 | 5 | 5 | TSW | TSW | 3.5 | **70.5** | **132.2** |
|  | 4 | 4.5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4.5 | 4.5 | 5 | 5 | TSW | TSW | 3.5 | **71** | **133** |
|  | 4 | 5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4.5 | 4.5 | 5 | 5 | TSW | TSW | 3.5 | **71.5** | **133.8** |
|  | 4 | 5 | 4 | 4.5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4.5 | 4.5 | 5 | 5 | TSW | TSW | 3.5 | **72** | **134.6** |
|  | 4 | 5 | 4 | 4.5 | 4 | 4 | 4 | 4 | 4 | 4 | 4.5 | 4 | 4.5 | 4.5 | 5 | 5 | TSW | TSW | 3.5 | **72.5** | **135.4** |
|  | 4 | 5 | 4 | 4.5 | 4 | 4.5 | 4 | 4 | 4 | 4 | 4.5 | 4 | 4.5 | 4.5 | 5 | 5 | TSW | TSW | 3.5 | **73** | **136.2** |
|  | 4 | 5 | 4 | 4.5 | 4 | 4.5 | 4 | 4 | 4 | 4.5 | 4.5 | 4 | 4.5 | 4.5 | 5 | 5 | TSW | TSW | 3.5 | **73.5** | **137** |
|  | 4 | 5 | 4 | 4.5 | 4 | 4.5 | 4 | 4 | 4 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 5 | 5 | TSW | TSW | 3.5 | **74** | **137.8** |
|  | 4 | 5 | 4 | 4.5 | 4.5 | 4.5 | 4 | 4 | 4 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 5 | 5 | TSW | TSW | 3.5 | **74.5** | **138.6** |
|  | 4 | 5 | 4 | 4.5 | 4.5 | 4.5 | 4 | 4.5 | 4 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 5 | 5 | TSW | TSW | 3.5 | **75** | **139.4** |
|  | 4 | 5 | 4 | 4.5 | 4.5 | 4.5 | 4 | 4.5 | 4 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 5 | 5.5 | TSW | TSW | 3.5 | **75.5** | **140.2** |
|  | 4 | 5 | 4 | 4.5 | 4.5 | 4.5 | 4 | 4.5 | 4 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 5 | 5.5 | TSW | TSW | 4 | **76** | **141** |
|  | 4 | 5 | 4 | 4.5 | 4.5 | 4.5 | 4 | 4.5 | 4 | 4.5 | 4.5 | 4.5 | 4.5 | 5 | 5 | 5.5 | TSW | TSW | 4 | **76.5** | **141.8** |
|  | 4 | 5 | 4.5 | 4.5 | 4.5 | 4.5 | 4 | 4.5 | 4 | 4.5 | 4.5 | 4.5 | 4.5 | 5 | 5 | 5.5 | TSW | TSW | 4 | **77** | **142.6** |
|  | 4 | 5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4 | 4.5 | 4.5 | 4.5 | 4.5 | 5 | 5 | 5.5 | TSW | TSW | 4 | **77.5** | **143.4** |
|  | 4 | 5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 5 | 5 | 5.5 | TSW | TSW | 4 | **78** | **144.2** |
|  | 4 | 5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 5 | 5.5 | 5.5 | TSW | TSW | 4 | **78.5** | **145** |
|  | 4 | 5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 5 | 5 | 5.5 | 5.5 | TSW | TSW | 4 | **79** | **145.8** |
|  | 4 | 5.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 5 | 5 | 5.5 | 5.5 | TSW | TSW | 4 | **79.5** | **146.6** |
|  | 4 | 5.5 | 4.5 | 5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 5 | 5 | 5.5 | 5.5 | TSW | TSW | 4 | **80** | **147.4** |
|  | 4 | 5.5 | 4.5 | 5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 5 | 4.5 | 5 | 5 | 5.5 | 5.5 | TSW | TSW | 4 | **80.5** | **148.2** |
|  | 4 | 5.5 | 4.5 | 5 | 4.5 | 5 | 4.5 | 4.5 | 4.5 | 4.5 | 5 | 4.5 | 5 | 5 | 5.5 | 5.5 | TSW | TSW | 4 | **81** | **149** |
|  | 4 | 5.5 | 4.5 | 5 | 4.5 | 5 | 4.5 | 4.5 | 4.5 | 5 | 5 | 4.5 | 5 | 5 | 5.5 | 5.5 | TSW | TSW | 4 | **81.5** | **149.8** |
|  | 4 | 5.5 | 4.5 | 5 | 4.5 | 5 | 4.5 | 4.5 | 4.5 | 5 | 5 | 5 | 5 | 5 | 5.5 | 5.5 | TSW | TSW | 4 | **82** | **150.6** |
|  | 4 | 5.5 | 4.5 | 5 | 5 | 5 | 4.5 | 4.5 | 4.5 | 5 | 5 | 5 | 5 | 5 | 5.5 | 5.5 | TSW | TSW | 4 | **82.5** | **151.4** |
|  | 4 | 5.5 | 4.5 | 5 | 5 | 5 | 4.5 | 5 | 4.5 | 5 | 5 | 5 | 5 | 5 | 5.5 | 5.5 | TSW | TSW | 4 | **83** | **152.2** |
|  | 4 | 5.5 | 4.5 | 5 | 5 | 5 | 4.5 | 5 | 4.5 | 5 | 5 | 5 | 5 | 5 | 5.5 | 6 | TSW | TSW | 4 | **83.5** | **153** |
|  | 4 | 5.5 | 4.5 | 5 | 5 | 5 | 4.5 | 5 | 4.5 | 5 | 5 | 5 | 5 | 5 | 5.5 | 6 | TSW | TSW | 4.5 | **84** | **153.8** |
|  | 4 | 5.5 | 4.5 | 5 | 5 | 5 | 4.5 | 5 | 4.5 | 5 | 5 | 5 | 5 | 5.5 | 5.5 | 6 | TSW | TSW | 4.5 | **84.5** | **154.6** |
|  | 4 | 5.5 | 5 | 5 | 5 | 5 | 4.5 | 5 | 4.5 | 5 | 5 | 5 | 5 | 5.5 | 5.5 | 6 | TSW | TSW | 4.5 | **85** | **155.4** |
|  | 4 | 5.5 | 5 | 5 | 5 | 5 | 5 | 5 | 4.5 | 5 | 5 | 5 | 5 | 5.5 | 5.5 | 6 | TSW | TSW | 4.5 | **85.5** | **156.2** |
|  | 4 | 5.5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5.5 | 5.5 | 6 | TSW | TSW | 4.5 | **86** | **157** |
|  | 4 | 5.5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5.5 | 6 | 6 | TSW | TSW | 4.5 | **86.5** | **157.8** |
|  | 4 | 5.5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5.5 | 5.5 | 6 | 6 | TSW | TSW | 4.5 | **87** | **158.6** |
|  | 4 | 6 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5.5 | 5.5 | 6 | 6 | TSW | TSW | 4.5 | **87.5** | **159.4** |
|  | 4 | 6 | 5 | 5.5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5.5 | 5.5 | 6 | 6 | TSW | TSW | 4.5 | **88** | **160.2** |
|  | 4 | 6 | 5 | 5.5 | 5 | 5 | 5 | 5 | 5 | 5 | 5.5 | 5 | 5.5 | 5.5 | 6 | 6 | TSW | TSW | 4.5 | **88.5** | **161** |
|  | 4 | 6 | 5 | 5.5 | 5 | 5.5 | 5 | 5 | 5 | 5 | 5.5 | 5 | 5.5 | 5.5 | 6 | 6 | TSW | TSW | 4.5 | **89** | **161.8** |
|  | 4 | 6 | 5 | 5.5 | 5 | 5.5 | 5 | 5 | 5 | 5.5 | 5.5 | 5 | 5.5 | 5.5 | 6 | 6 | TSW | TSW | 4.5 | **89.5** | **162.6** |
|  | 4 | 6 | 5 | 5.5 | 5 | 5.5 | 5 | 5 | 5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 6 | 6 | TSW | TSW | 4.5 | **90** | **163.4** |
|  | 4 | 6 | 5 | 5.5 | 5.5 | 5.5 | 5 | 5 | 5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 6 | 6 | TSW | TSW | 4.5 | **90.5** | **164.2** |
|  | 4 | 6 | 5 | 5.5 | 5.5 | 5.5 | 5 | 5.5 | 5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 6 | 6 | TSW | TSW | 4.5 | **91** | **165** |
|  | 4 | 6 | 5 | 5.5 | 5.5 | 5.5 | 5 | 5.5 | 5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 6 | 6.5 | TSW | TSW | 4.5 | **91.5** | **165.8** |
|  | 4 | 6 | 5 | 5.5 | 5.5 | 5.5 | 5 | 5.5 | 5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 6 | 6.5 | TSW | TSW | 5 | **92** | **166.6** |
|  | 4 | 6 | 5 | 5.5 | 5.5 | 5.5 | 5 | 5.5 | 5 | 5.5 | 5.5 | 5.5 | 5.5 | 6 | 6 | 6.5 | TSW | TSW | 5 | **92.5** | **167.4** |
|  | 4 | 6 | 5.5 | 5.5 | 5.5 | 5.5 | 5 | 5.5 | 5 | 5.5 | 5.5 | 5.5 | 5.5 | 6 | 6 | 6.5 | TSW | TSW | 5 | **93** | **168.2** |
|  | 4 | 6 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5 | 5.5 | 5.5 | 5.5 | 5.5 | 6 | 6 | 6.5 | TSW | TSW | 5 | **93.5** | **169** |
|  | 4 | 6 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 6 | 6 | 6.5 | TSW | TSW | 5 | **94** | **169.8** |
|  | 4 | 6 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 6 | 6.5 | 6.5 | TSW | TSW | 5 | **94.5** | **170.6** |
|  | 4 | 6 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 6 | 6 | 6.5 | 6.5 | TSW | TSW | 5 | **95** | **171.4** |
|  | 4 | 6 | 5.5 | 6 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 6 | 6 | 6.5 | 6.5 | TSW | TSW | 5 | **95.5** | **172.2** |
|  | 4 | 6 | 5.5 | 6 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 6 | 5.5 | 6 | 6 | 6.5 | 6.5 | TSW | TSW | 5 | **96** | **173** |
|  | 4 | 6 | 5.5 | 6 | 5.5 | 6 | 5.5 | 5.5 | 5.5 | 5.5 | 6 | 5.5 | 6 | 6 | 6.5 | 6.5 | TSW | TSW | 5 | **96.5** | **173.8** |
|  | 4 | 6 | 5.5 | 6 | 5.5 | 6 | 5.5 | 5.5 | 5.5 | 6 | 6 | 5.5 | 6 | 6 | 6.5 | 6.5 | TSW | TSW | 5 | **97** | **174.6** |
|  | 4 | 6 | 5.5 | 6 | 5.5 | 6 | 5.5 | 5.5 | 5.5 | 6 | 6 | 6 | 6 | 6 | 6.5 | 6.5 | TSW | TSW | 5 | **97.5** | **175.4** |
|  | 4 | 6 | 5.5 | 6 | 6 | 6 | 5.5 | 5.5 | 5.5 | 6 | 6 | 6 | 6 | 6 | 6.5 | 6.5 | TSW | TSW | 5 | **98** | **176.2** |
|  | 4 | 6 | 5.5 | 6 | 6 | 6 | 5.5 | 6 | 5.5 | 6 | 6 | 6 | 6 | 6 | 6.5 | 6.5 | TSW | TSW | 5 | **98.5** | **177** |
|  | 4 | 6 | 5.5 | 6 | 6 | 6 | 5.5 | 6 | 5.5 | 6 | 6 | 6 | 6 | 6 | 6.5 | 7 | TSW | TSW | 5 | **99** | **177.8** |
|  | 4 | 6 | 5.5 | 6 | 6 | 6 | 5.5 | 6 | 5.5 | 6 | 6 | 6 | 6 | 6 | 6.5 | 7 | TSW | TSW | 5.5 | **99.5** | **178.6** |
|  | 4 | 6 | 5.5 | 6 | 6 | 6 | 5.5 | 6 | 5.5 | 6 | 6 | 6 | 6 | 6.5 | 6.5 | 7 | TSW | TSW | 5.5 | **100** | **179.4** |
|  | 4 | 6 | 6 | 6 | 6 | 6 | 5.5 | 6 | 5.5 | 6 | 6 | 6 | 6 | 6.5 | 6.5 | 7 | TSW | TSW | 5.5 | **100.5** | **180.2** |
|  | 4 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 5.5 | 6 | 6 | 6 | 6 | 6.5 | 6.5 | 7 | TSW | TSW | 5.5 | **101** | **181** |
|  | 4 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6.5 | 6.5 | 7 | TSW | TSW | 5.5 | **101.5** | **181.8** |
|  | 4 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6.5 | 7 | 7 | TSW | TSW | 5.5 | **102** | **182.6** |
|  | 4 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6.5 | 6.5 | 7 | 7 | TSW | TSW | 5.5 | **102.5** | **183.4** |
|  | 4 | 6 | 6 | 6.5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6.5 | 6.5 | 7 | 7 | TSW | TSW | 5.5 | **103** | **184.2** |
|  | 4 | 6 | 6 | 6.5 | 6 | 6 | 6 | 6 | 6 | 6 | 6.5 | 6 | 6.5 | 6.5 | 7 | 7 | TSW | TSW | 5.5 | **103.5** | **185** |
|  | 4 | 6 | 6 | 6.5 | 6 | 6.5 | 6 | 6 | 6 | 6 | 6.5 | 6 | 6.5 | 6.5 | 7 | 7 | TSW | TSW | 5.5 | **104** | **185.8** |
|  | 4 | 6 | 6 | 6.5 | 6 | 6.5 | 6 | 6 | 6 | 6.5 | 6.5 | 6 | 6.5 | 6.5 | 7 | 7 | TSW | TSW | 5.5 | **104.5** | **186.6** |
|  | 4 | 6 | 6 | 6.5 | 6 | 6.5 | 6 | 6 | 6 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 7 | 7 | TSW | TSW | 5.5 | **105** | **187.4** |
|  | 4 | 6 | 6 | 6.5 | 6.5 | 6.5 | 6 | 6 | 6 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 7 | 7 | TSW | TSW | 5.5 | **105.5** | **188.2** |
|  | 4 | 6 | 6 | 6.5 | 6.5 | 6.5 | 6 | 6.5 | 6 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 7 | 7 | TSW | TSW | 5.5 | **106** | **189** |
|  | 4 | 6 | 6 | 6.5 | 6.5 | 6.5 | 6 | 6.5 | 6 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 7 | 7.5 | TSW | TSW | 5.5 | **106.5** | **189.8** |
|  | 4 | 6 | 6 | 6.5 | 6.5 | 6.5 | 6 | 6.5 | 6 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 7 | 7.5 | TSW | TSW | 6 | **107** | **190.6** |
|  | 4 | 6 | 6 | 6.5 | 6.5 | 6.5 | 6 | 6.5 | 6 | 6.5 | 6.5 | 6.5 | 6.5 | 7 | 7 | 7.5 | TSW | TSW | 6 | **107.5** | **191.4** |
|  | 4 | 6 | 6.5 | 6.5 | 6.5 | 6.5 | 6 | 6.5 | 6 | 6.5 | 6.5 | 6.5 | 6.5 | 7 | 7 | 7.5 | TSW | TSW | 6 | **108** | **192.2** |
|  | 4 | 6 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6 | 6.5 | 6.5 | 6.5 | 6.5 | 7 | 7 | 7.5 | TSW | TSW | 6 | **108.5** | **193** |
|  | 4 | 6 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 7 | 7 | 7.5 | TSW | TSW | 6 | **109** | **193.8** |
|  | 4 | 6 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 7 | 7.5 | 7.5 | TSW | TSW | 6 | **109.5** | **194.6** |
|  | 4 | 6 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 7 | 7 | 7.5 | 7.5 | TSW | TSW | 6 | **110** | **195.4** |
|  | 4 | 6 | 6.5 | 7 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 7 | 7 | 7.5 | 7.5 | TSW | TSW | 6 | **110.5** | **196.2** |
|  | 4 | 6 | 6.5 | 7 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 7 | 6.5 | 7 | 7 | 7.5 | 7.5 | TSW | TSW | 6 | **111** | **197** |
|  | 4 | 6 | 6.5 | 7 | 6.5 | 7 | 6.5 | 6.5 | 6.5 | 6.5 | 7 | 6.5 | 7 | 7 | 7.5 | 7.5 | TSW | TSW | 6 | **111.5** | **197.8** |
|  | 4 | 6 | 6.5 | 7 | 6.5 | 7 | 6.5 | 6.5 | 6.5 | 7 | 7 | 6.5 | 7 | 7 | 7.5 | 7.5 | TSW | TSW | 6 | **112** | **198.6** |
|  | 4 | 6 | 6.5 | 7 | 6.5 | 7 | 6.5 | 6.5 | 6.5 | 7 | 7 | 7 | 7 | 7 | 7.5 | 7.5 | TSW | TSW | 6 | **112.5** | **199.4** |
|  | 4 | 6 | 6.5 | 7 | 7 | 7 | 6.5 | 6.5 | 6.5 | 7 | 7 | 7 | 7 | 7 | 7.5 | 7.5 | TSW | TSW | 6 | **113** | **200.2** |
|  | 4 | 6 | 6.5 | 7 | 7 | 7 | 6.5 | 7 | 6.5 | 7 | 7 | 7 | 7 | 7 | 7.5 | 7.5 | TSW | TSW | 6 | **113.5** | **201** |
|  | 4 | 6 | 6.5 | 7 | 7 | 7 | 6.5 | 7 | 6.5 | 7 | 7 | 7 | 7 | 7 | 7.5 | 8 | TSW | TSW | 6 | **114** | **201.8** |
|  | 4 | 6 | 6.5 | 7 | 7 | 7 | 6.5 | 7 | 6.5 | 7 | 7 | 7 | 7 | 7 | 7.5 | 8 | TSW | TSW | 6.5 | **114.5** | **202.6** |
|  | 4 | 6 | 6.5 | 7 | 7 | 7 | 6.5 | 7 | 6.5 | 7 | 7 | 7 | 7 | 7.5 | 7.5 | 8 | TSW | TSW | 6.5 | **115** | **203.4** |
|  | 4 | 6 | 7 | 7 | 7 | 7 | 6.5 | 7 | 6.5 | 7 | 7 | 7 | 7 | 7.5 | 7.5 | 8 | TSW | TSW | 6.5 | **115.5** | **204.2** |
|  | 4 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 6.5 | 7 | 7 | 7 | 7 | 7.5 | 7.5 | 8 | TSW | TSW | 6.5 | **116** | **205** |
|  | 4 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7.5 | 7.5 | 8 | TSW | TSW | 6.5 | **116.5** | **205.8** |
|  | 4 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7.5 | 8 | 8 | TSW | TSW | 6.5 | **117** | **206.6** |
|  | 4 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7.5 | 7.5 | 8 | 8 | TSW | TSW | 6.5 | **117.5** | **207.4** |
|  | 4 | 6 | 7 | 7.5 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7.5 | 7.5 | 8 | 8 | TSW | TSW | 6.5 | **118** | **208.2** |
|  | 4 | 6 | 7 | 7.5 | 7 | 7 | 7 | 7 | 7 | 7 | 7.5 | 7 | 7.5 | 7.5 | 8 | 8 | TSW | TSW | 6.5 | **118.5** | **209** |
|  | 4 | 6 | 7 | 7.5 | 7 | 7.5 | 7 | 7 | 7 | 7 | 7.5 | 7 | 7.5 | 7.5 | 8 | 8 | TSW | TSW | 6.5 | **119** | **209.8** |
|  | 4 | 6 | 7 | 7.5 | 7 | 7.5 | 7 | 7 | 7 | 7.5 | 7.5 | 7 | 7.5 | 7.5 | 8 | 8 | TSW | TSW | 6.5 | **119.5** | **210.6** |
|  | 4 | 6 | 7 | 7.5 | 7 | 7.5 | 7 | 7 | 7 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 8 | 8 | TSW | TSW | 6.5 | **120** | **211.4** |
|  | 4 | 6 | 7 | 7.5 | 7.5 | 7.5 | 7 | 7 | 7 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 8 | 8 | TSW | TSW | 6.5 | **120.5** | **212.2** |
|  | 4 | 6 | 7 | 7.5 | 7.5 | 7.5 | 7 | 7.5 | 7 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 8 | 8 | TSW | TSW | 6.5 | **121** | **213** |
|  | 4 | 6 | 7 | 7.5 | 7.5 | 7.5 | 7 | 7.5 | 7 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 8 | 8.5 | TSW | TSW | 6.5 | **121.5** | **213.8** |
|  | 4 | 6 | 7 | 7.5 | 7.5 | 7.5 | 7 | 7.5 | 7 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 8 | 8.5 | TSW | TSW | 7 | **122** | **214.6** |
|  | 4 | 6 | 7 | 7.5 | 7.5 | 7.5 | 7 | 7.5 | 7 | 7.5 | 7.5 | 7.5 | 7.5 | 8 | 8 | 8.5 | TSW | TSW | 7 | **122.5** | **215.4** |
|  | 4 | 6 | 7.5 | 7.5 | 7.5 | 7.5 | 7 | 7.5 | 7 | 7.5 | 7.5 | 7.5 | 7.5 | 8 | 8 | 8.5 | TSW | TSW | 7 | **123** | **216.2** |
|  | 4 | 6 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7 | 7.5 | 7.5 | 7.5 | 7.5 | 8 | 8 | 8.5 | TSW | TSW | 7 | **123.5** | **217** |
|  | 4 | 6 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 8 | 8 | 8.5 | TSW | TSW | 7 | **124** | **217.8** |
|  | 4 | 6 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 8 | 8.5 | 8.5 | TSW | TSW | 7 | **124.5** | **218.6** |
|  | 4 | 6 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 8 | 8 | 8.5 | 8.5 | TSW | TSW | 7 | **125** | **219.4** |
|  | 4 | 6 | 7.5 | 8 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 8 | 8 | 8.5 | 8.5 | TSW | TSW | 7 | **125.5** | **220.2** |
|  | 4 | 6 | 7.5 | 8 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 8 | 7.5 | 8 | 8 | 8.5 | 8.5 | TSW | TSW | 7 | **126** | **221** |
|  | 4 | 6 | 7.5 | 8 | 7.5 | 8 | 7.5 | 7.5 | 7.5 | 7.5 | 8 | 7.5 | 8 | 8 | 8.5 | 8.5 | TSW | TSW | 7 | **126.5** | **221.8** |
|  | 4 | 6 | 7.5 | 8 | 7.5 | 8 | 7.5 | 7.5 | 7.5 | 8 | 8 | 7.5 | 8 | 8 | 8.5 | 8.5 | TSW | TSW | 7 | **127** | **222.6** |
|  | 4 | 6 | 7.5 | 8 | 7.5 | 8 | 7.5 | 7.5 | 7.5 | 8 | 8 | 8 | 8 | 8 | 8.5 | 8.5 | TSW | TSW | 7 | **127.5** | **223.4** |
|  | 4 | 6 | 7.5 | 8 | 8 | 8 | 7.5 | 7.5 | 7.5 | 8 | 8 | 8 | 8 | 8 | 8.5 | 8.5 | TSW | TSW | 7 | **128** | **224.2** |
|  | 4 | 6 | 7.5 | 8 | 8 | 8 | 7.5 | 8 | 7.5 | 8 | 8 | 8 | 8 | 8 | 8.5 | 8.5 | TSW | TSW | 7 | **128.5** | **225** |
|  | 4 | 6 | 7.5 | 8 | 8 | 8 | 7.5 | 8 | 7.5 | 8 | 8 | 8 | 8 | 8 | 8.5 | 9 | TSW | TSW | 7 | **129** | **225.8** |
|  | 4 | 6 | 7.5 | 8 | 8 | 8 | 7.5 | 8 | 7.5 | 8 | 8 | 8 | 8 | 8 | 8.5 | 9 | TSW | TSW | 7.5 | **129.5** | **226.6** |
|  | 4 | 6 | 7.5 | 8 | 8 | 8 | 7.5 | 8 | 7.5 | 8 | 8 | 8 | 8 | 8.5 | 8.5 | 9 | TSW | TSW | 7.5 | **130** | **227.4** |
|  | 4 | 6 | 8 | 8 | 8 | 8 | 7.5 | 8 | 7.5 | 8 | 8 | 8 | 8 | 8.5 | 8.5 | 9 | TSW | TSW | 7.5 | **130.5** | **228.2** |
|  | 4 | 6 | 8 | 8 | 8 | 8 | 8 | 8 | 7.5 | 8 | 8 | 8 | 8 | 8.5 | 8.5 | 9 | TSW | TSW | 7.5 | **131** | **229** |
|  | 4 | 6 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8.5 | 8.5 | 9 | TSW | TSW | 7.5 | **131.5** | **229.8** |
|  | 4 | 6 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8.5 | 9 | 9 | TSW | TSW | 7.5 | **132** | **230.6** |
|  | 4 | 6 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8.5 | 8.5 | 9 | 9 | TSW | TSW | 7.5 | **132.5** | **231.4** |
|  | 4 | 6 | 8 | 8.5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8.5 | 8.5 | 9 | 9 | TSW | TSW | 7.5 | **133** | **232.2** |
|  | 4 | 6 | 8 | 8.5 | 8 | 8 | 8 | 8 | 8 | 8 | 8.5 | 8 | 8.5 | 8.5 | 9 | 9 | TSW | TSW | 7.5 | **133.5** | **233** |
|  | 4 | 6 | 8 | 8.5 | 8 | 8.5 | 8 | 8 | 8 | 8 | 8.5 | 8 | 8.5 | 8.5 | 9 | 9 | TSW | TSW | 7.5 | **134** | **233.8** |
|  | 4 | 6 | 8 | 8.5 | 8 | 8.5 | 8 | 8 | 8 | 8.5 | 8.5 | 8 | 8.5 | 8.5 | 9 | 9 | TSW | TSW | 7.5 | **134.5** | **234.6** |
|  | 4 | 6 | 8 | 8.5 | 8 | 8.5 | 8 | 8 | 8 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 9 | 9 | TSW | TSW | 7.5 | **135** | **235.4** |
|  | 4 | 6 | 8 | 8.5 | 8.5 | 8.5 | 8 | 8 | 8 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 9 | 9 | TSW | TSW | 7.5 | **135.5** | **236.2** |
|  | 4 | 6 | 8 | 8.5 | 8.5 | 8.5 | 8 | 8.5 | 8 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 9 | 9 | TSW | TSW | 7.5 | **136** | **237** |
|  | 4 | 6 | 8 | 8.5 | 8.5 | 8.5 | 8 | 8.5 | 8 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 9 | 9.5 | TSW | TSW | 7.5 | **136.5** | **237.8** |
|  | 4 | 6 | 8 | 8.5 | 8.5 | 8.5 | 8 | 8.5 | 8 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 9 | 9.5 | TSW | TSW | 8 | **137** | **238.6** |
|  | 4 | 6 | 8 | 8.5 | 8.5 | 8.5 | 8 | 8.5 | 8 | 8.5 | 8.5 | 8.5 | 8.5 | 9 | 9 | 9.5 | TSW | TSW | 8 | **137.5** | **239.4** |
|  | 4 | 6 | 8 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8 | 8.5 | 8.5 | 8.5 | 8.5 | 9 | 9 | 9.5 | TSW | TSW | 8 | **138** | **240.2** |
|  | 4 | 6 | 8 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 9 | 9 | 9.5 | TSW | TSW | 8 | **138.5** | **241** |
|  | 4 | 6 | 8 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 9 | 9.5 | 9.5 | TSW | TSW | 8 | **139** | **241.8** |
|  | 4 | 6 | 8 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 9 | 9 | 9.5 | 9.5 | TSW | TSW | 8 | **139.5** | **242.6** |
|  | 4 | 6 | 8 | 9 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 9 | 9 | 9.5 | 9.5 | TSW | TSW | 8 | **140** | **243.4** |
|  | 4 | 6 | 8 | 9 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 9 | 8.5 | 9 | 9 | 9.5 | 9.5 | TSW | TSW | 8 | **140.5** | **244.2** |
|  | 4 | 6 | 8 | 9 | 8.5 | 9 | 8.5 | 8.5 | 8.5 | 8.5 | 9 | 8.5 | 9 | 9 | 9.5 | 9.5 | TSW | TSW | 8 | **141** | **245** |
|  | 4 | 6 | 8 | 9 | 8.5 | 9 | 8.5 | 8.5 | 8.5 | 9 | 9 | 8.5 | 9 | 9 | 9.5 | 9.5 | TSW | TSW | 8 | **141.5** | **245.8** |
|  | 4 | 6 | 8 | 9 | 8.5 | 9 | 8.5 | 8.5 | 8.5 | 9 | 9 | 9 | 9 | 9 | 9.5 | 9.5 | TSW | TSW | 8 | **142** | **246.6** |
|  | 4 | 6 | 8 | 9 | 9 | 9 | 8.5 | 8.5 | 8.5 | 9 | 9 | 9 | 9 | 9 | 9.5 | 9.5 | TSW | TSW | 8 | **142.5** | **247.4** |
|  | 4 | 6 | 8 | 9 | 9 | 9 | 8.5 | 9 | 8.5 | 9 | 9 | 9 | 9 | 9 | 9.5 | 9.5 | TSW | TSW | 8 | **143** | **248.2** |
|  | 4 | 6 | 8 | 9 | 9 | 9 | 8.5 | 9 | 8.5 | 9 | 9 | 9 | 9 | 9 | 9.5 | 10 | TSW | TSW | 8 | **143.5** | **249** |
|  | 4 | 6 | 8 | 9 | 9 | 9 | 8.5 | 9 | 8.5 | 9 | 9 | 9 | 9 | 9 | 9.5 | 10 | TSW | TSW | 8.5 | **144** | **249.8** |
|  | 4 | 6 | 8 | 9 | 9 | 9 | 8.5 | 9 | 8.5 | 9 | 9 | 9 | 9 | 9.5 | 9.5 | 10 | TSW | TSW | 8.5 | **144.5** | **250.6** |
|  | 4 | 6 | 8 | 9 | 9 | 9 | 9 | 9 | 8.5 | 9 | 9 | 9 | 9 | 9.5 | 9.5 | 10 | TSW | TSW | 8.5 | **145** | **251.4** |
|  | 4 | 6 | 8 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9.5 | 9.5 | 10 | TSW | TSW | 8.5 | **145.5** | **252.2** |
|  | 4 | 6 | 8 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9.5 | 10 | 10 | TSW | TSW | 8.5 | **146** | **253** |
|  | 4 | 6 | 8 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9.5 | 9.5 | 10 | 10 | TSW | TSW | 8.5 | **146.5** | **253.8** |
|  | 4 | 6 | 8 | 9.5 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9.5 | 9.5 | 10 | 10 | TSW | TSW | 8.5 | **147** | **254.6** |
|  | 4 | 6 | 8 | 9.5 | 9 | 9 | 9 | 9 | 9 | 9 | 9.5 | 9 | 9.5 | 9.5 | 10 | 10 | TSW | TSW | 8.5 | **147.5** | **255.4** |
|  | 4 | 6 | 8 | 9.5 | 9 | 9.5 | 9 | 9 | 9 | 9 | 9.5 | 9 | 9.5 | 9.5 | 10 | 10 | TSW | TSW | 8.5 | **148** | **256.2** |
|  | 4 | 6 | 8 | 9.5 | 9 | 9.5 | 9 | 9 | 9 | 9.5 | 9.5 | 9 | 9.5 | 9.5 | 10 | 10 | TSW | TSW | 8.5 | **148.5** | **257** |
|  | 4 | 6 | 8 | 9.5 | 9 | 9.5 | 9 | 9 | 9 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 10 | 10 | TSW | TSW | 8.5 | **149** | **257.8** |
|  | 4 | 6 | 8 | 9.5 | 9.5 | 9.5 | 9 | 9 | 9 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 10 | 10 | TSW | TSW | 8.5 | **149.5** | **258.6** |
|  | 4 | 6 | 8 | 9.5 | 9.5 | 9.5 | 9 | 9.5 | 9 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 10 | 10 | TSW | TSW | 8.5 | **150** | **259.4** |
|  | 4 | 6 | 8 | 9.5 | 9.5 | 9.5 | 9 | 9.5 | 9 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 10 | 11 | TSW | TSW | 8.5 | **151** | **260.2** |
|  | 4 | 6 | 8 | 9.5 | 9.5 | 9.5 | 9 | 9.5 | 9 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 10 | 11 | TSW | TSW | 9 | **151.5** | **261** |
|  | 4 | 6 | 8 | 9.5 | 9.5 | 9.5 | 9 | 9.5 | 9 | 9.5 | 9.5 | 9.5 | 9.5 | 10 | 10 | 11 | TSW | TSW | 9 | **152** | **261.8** |
|  | 4 | 6 | 8 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9 | 9.5 | 9.5 | 9.5 | 9.5 | 10 | 10 | 11 | TSW | TSW | 9 | **152.5** | **262.6** |
|  | 4 | 6 | 8 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 10 | 10 | 11 | TSW | TSW | 9 | **153** | **263.4** |
|  | 4 | 6 | 8 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 10 | 11 | 11 | TSW | TSW | 9 | **154** | **264.2** |
|  | 4 | 6 | 8 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 10 | 10 | 11 | 11 | TSW | TSW | 9 | **154.5** | **265** |
|  | 4 | 6 | 8 | 10 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 10 | 10 | 11 | 11 | TSW | TSW | 9 | **155** | **265.8** |
|  | 4 | 6 | 8 | 10 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 10 | 9.5 | 10 | 10 | 11 | 11 | TSW | TSW | 9 | **155.5** | **266.6** |
|  | 4 | 6 | 8 | 10 | 9.5 | 10 | 9.5 | 9.5 | 9.5 | 9.5 | 10 | 9.5 | 10 | 10 | 11 | 11 | TSW | TSW | 9 | **156** | **267.4** |
|  | 4 | 6 | 8 | 10 | 9.5 | 10 | 9.5 | 9.5 | 9.5 | 10 | 10 | 9.5 | 10 | 10 | 11 | 11 | TSW | TSW | 9 | **156.5** | **268.2** |
|  | 4 | 6 | 8 | 10 | 9.5 | 10 | 9.5 | 9.5 | 9.5 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | TSW | TSW | 9 | **157** | **269** |
|  | 4 | 6 | 8 | 10 | 10 | 10 | 9.5 | 9.5 | 9.5 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | TSW | TSW | 9 | **157.5** | **269.8** |
|  | 4 | 6 | 8 | 10 | 10 | 10 | 9.5 | 10 | 9.5 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | TSW | TSW | 9 | **158** | **270.6** |
|  | 4 | 6 | 8 | 10 | 10 | 10 | 9.5 | 10 | 9.5 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | TSW | TSW | 9 | **158** | **271.4** |
|  | 4 | 6 | 8 | 10 | 10 | 10 | 9.5 | 10 | 9.5 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | TSW | TSW | 9.5 | **158.5** | **272.2** |
|  | 4 | 6 | 8 | 10 | 10 | 10 | 9.5 | 10 | 9.5 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | TSW | TSW | 9.5 | **159.5** | **273** |
|  | 4 | 6 | 8 | 10 | 10 | 10 | 10 | 10 | 9.5 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | TSW | TSW | 9.5 | **160** | **273.8** |
|  | 4 | 6 | 8 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | TSW | TSW | 9.5 | **160.5** | **274.6** |
|  | 4 | 6 | 8 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | TSW | TSW | 9.5 | **160.5** | **275.4** |
|  | 4 | 6 | 8 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | 11 | TSW | TSW | 9.5 | **161.5** | **276.2** |
|  | 4 | 6 | 8 | 11 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | 11 | TSW | TSW | 9.5 | **162.5** | **277** |
|  | 4 | 6 | 8 | 11 | 10 | 10 | 10 | 10 | 10 | 10 | 11 | 10 | 11 | 11 | 11 | 11 | TSW | TSW | 9.5 | **163.5** | **277.8** |
|  | 4 | 6 | 8 | 11 | 10 | 11 | 10 | 10 | 10 | 10 | 11 | 10 | 11 | 11 | 11 | 11 | TSW | TSW | 9.5 | **164.5** | **278.6** |
|  | 4 | 6 | 8 | 11 | 10 | 11 | 10 | 10 | 10 | 11 | 11 | 10 | 11 | 11 | 11 | 11 | TSW | TSW | 9.5 | **165.5** | **279.4** |
|  | 4 | 6 | 8 | 11 | 10 | 11 | 10 | 10 | 10 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | TSW | TSW | 9.5 | **166.5** | **280.2** |
|  | 4 | 6 | 8 | 11 | 11 | 11 | 10 | 10 | 10 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | TSW | TSW | 9.5 | **167.5** | **281** |
|  | 4 | 6 | 8 | 11 | 11 | 11 | 10 | 11 | 10 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | TSW | TSW | 9.5 | **168.5** | **281.8** |
|  | 4 | 6 | 8 | 11 | 11 | 11 | 10 | 11 | 10 | 11 | 11 | 11 | 11 | 11 | 11 | 12 | TSW | TSW | 9.5 | **169.5** | **282.6** |
|  | 4 | 6 | 8 | 11 | 11 | 11 | 10 | 11 | 10 | 11 | 11 | 11 | 11 | 11 | 11 | 12 | TSW | TSW | 10 | **170** | **283.4** |
|  | 4 | 6 | 8 | 11 | 11 | 11 | 10 | 11 | 10 | 11 | 11 | 11 | 11 | 11 | 11 | 12 | TSW | TSW | 10 | **170** | **284.2** |
|  | 4 | 6 | 8 | 11 | 11 | 11 | 11 | 11 | 10 | 11 | 11 | 11 | 11 | 11 | 11 | 12 | TSW | TSW | 10 | **171** | **285** |
|  | 4 | 6 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 12 | TSW | TSW | 10 | **172** | **285.8** |
|  | 4 | 6 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 12 | 12 | TSW | TSW | 10 | **173** | **286.6** |
|  | 4 | 6 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 12 | 12 | TSW | TSW | 10 | **173** | **287.4** |
|  | 4 | 6 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 12 | 12 | TSW | TSW | 10 | **173** | **288.2** |
|  | 4 | 6 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 12 | 12 | TSW | TSW | 10 | **173** | **289** |
|  | 4 | 6 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 12 | 12 | TSW | TSW | 10 | **173** | **289.8** |
|  | 4 | 6 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 12 | 12 | TSW | TSW | 10 | **173** | **290.6** |
|  | 4 | 6 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 12 | 12 | TSW | TSW | 10 | **173** | **291.4** |
|  | 4 | 6 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 12 | 12 | TSW | TSW | 10 | **173** | **292.2** |
|  | 4 | 6 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 12 | 12 | TSW | TSW | 10 | **173** | **293** |
|  | 4 | 6 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 12 | 12 | TSW | TSW | 10 | **173** | **293.8** |
|  | 4 | 6 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 12 | 12 | TSW | TSW | 10.5 | **173.5** | **294.6** |
|  | 4 | 6 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 12 | 12 | 12 | TSW | TSW | 10.5 | **174.5** | **295.4** |
|  | 4 | 6 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 12 | 12 | 12 | TSW | TSW | 10.5 | **174.5** | **296.2** |
|  | 4 | 6 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 12 | 12 | 12 | TSW | TSW | 10.5 | **174.5** | **297** |
|  | 4 | 6 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 12 | 12 | 12 | TSW | TSW | 10.5 | **174.5** | **297.8** |
|  | 4 | 6 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 12 | 12 | 12 | 12 | TSW | TSW | 10.5 | **175.5** | **298.6** |
|  | 4 | 6 | 8 | 12 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 12 | 12 | 12 | 12 | TSW | TSW | 10.5 | **176.5** | **299.4** |
|  | 4 | 6 | 8 | 12 | 11 | 11 | 11 | 11 | 11 | 11 | 12 | 11 | 12 | 12 | 12 | 12 | TSW | TSW | 10.5 | **177.5** | **300.2** |
|  | 4 | 6 | 8 | 12 | 11 | 12 | 11 | 11 | 11 | 11 | 12 | 11 | 12 | 12 | 12 | 12 | TSW | TSW | 10.5 | **178.5** | **301** |
|  | 4 | 6 | 8 | 12 | 11 | 12 | 11 | 11 | 11 | 12 | 12 | 11 | 12 | 12 | 12 | 12 | TSW | TSW | 10.5 | **179.5** | **301.8** |
|  | 4 | 6 | 8 | 12 | 11 | 12 | 11 | 11 | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | TSW | TSW | 10.5 | **180.5** | **302.6** |
|  | 4 | 6 | 8 | 12 | 12 | 12 | 11 | 11 | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | TSW | TSW | 10.5 | **181.5** | **303.4** |
|  | 4 | 6 | 8 | 12 | 12 | 12 | 11 | 12 | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | TSW | TSW | 10.5 | **182.5** | **304.2** |
|  | 4 | 6 | 8 | 12 | 12 | 12 | 11 | 12 | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | TSW | TSW | 11 | **183** | **305** |
|  | 4 | 6 | 8 | 12 | 12 | 12 | 12 | 12 | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | TSW | TSW | 11 | **184** | **305.8** |
|  | 4 | 6 | 8 | 12 | 12 | 12 | 12 | 12 | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | TSW | TSW | 11 | **184** | **306.6** |
|  | 4 | 6 | 8 | 12 | 12 | 12 | 12 | 12 | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | TSW | TSW | 11 | **184** | **307.4** |
|  | 4 | 6 | 8 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | TSW | TSW | 11 | **185** | **308.2** |
|  | 4 | 6 | 8 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | TSW | TSW | 11 | **185** | **309** |
|  | 4 | 6 | 8 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | TSW | TSW | 11 | **185** | **309.8** |
|  | 4 | 6 | 8 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | TSW | TSW | 11 | **185** | **310.6** |
|  | 4 | 6 | 8 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | TSW | TSW | 11 | **185** | **311.4** |
|  | 4 | 6 | 8 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | TSW | TSW | 11 | **185** | **312.2** |
|  | 4 | 6 | 8 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | TSW | TSW | 11 | **185** | **313** |
|  | 4 | 6 | 8 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | TSW | TSW | 11 | **185** | **313.8** |
|  | 4 | 6 | 8 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | TSW | TSW | 11 | **185** | **314.6** |
|  | 4 | 6 | 8 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | TSW | TSW | 11 | **185** | **315.4** |
| 1 | 4 | 6 | 8 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | TSW | TSW | 11 | **186** | **317** |
| 2 | 4 | 6 | 8 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | TSW | TSW | 11 | **187** | **318.6** |
| 3 | 4 | 6 | 8 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | TSW | TSW | 11 | **188** | **320.2** |
| 3 | 4 | 6 | 9 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | TSW | TSW | 11 | **189** | **321.8** |
| 4 | 4 | 6 | 9 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | TSW | TSW | 11 | **190** | **323.4** |
| 4 | 5 | 6 | 9 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | TSW | TSW | 11 | **191** | **325** |
| 4 | 5 | 7 | 9 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | TSW | TSW | 11 | **192** | **326.6** |
| 4 | 5 | 7 | 10 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | TSW | TSW | 11 | **193** | **328.2** |
| 5 | 5 | 7 | 10 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | TSW | TSW | 11 | **194** | **329.8** |
| 5 | 6 | 7 | 10 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | TSW | TSW | 11 | **195** | **331.4** |
| 5 | 6 | 8 | 10 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | TSW | TSW | 11 | **196** | **333** |
| 5 | 6 | 8 | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | TSW | TSW | 11 | **197** | **334.6** |
| 6 | 6 | 8 | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | TSW | TSW | 11 | **198** | **336.2** |
| 6 | 7 | 8 | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | TSW | TSW | 11 | **199** | **337.8** |
| 6 | 7 | 9 | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | TSW | TSW | 11 | **200** | **339.4** |
| 6 | 7 | 9 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | TSW | TSW | 11 | **201** | **341** |
| 7 | 7 | 9 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | TSW | TSW | 11 | **202** | **342.6** |
| 7 | 8 | 9 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | TSW | TSW | 11 | **203** | **344.2** |
| 7 | 8 | 10 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | TSW | TSW | 11 | **204** | **345.8** |
| 8 | 8 | 10 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | TSW | TSW | 11 | **205** | **347.4** |
| 8 | 9 | 10 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | TSW | TSW | 11 | **206** | **349** |
| 8 | 9 | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | TSW | TSW | 11 | **207** | **350.6** |
| 9 | 9 | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | TSW | TSW | 11 | **208** | **352.2** |
| 9 | 10 | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | TSW | TSW | 11 | **209** | **353.8** |
| 10 | 10 | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | TSW | TSW | 11 | **210** | **355.4** |
| 10 | 11 | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | TSW | TSW | 11 | **211** | **357** |
| 10 | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | TSW | TSW | 11 | **212** | **358.6** |
| 11 | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | TSW | TSW | 11 | **213** | **360.2** |
| 11 | 11 | 13 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | TSW | TSW | 11 | **214** | **361.8** |
| 11 | 11 | 13 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 13 | TSW | TSW | 11 | **215** | **363.4** |
| 11 | 11 | 13 | 13 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 13 | TSW | TSW | 11 | **216** | **365** |
| 11 | 11 | 13 | 13 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 13 | 12 | 13 | TSW | TSW | 11 | **217** | **366.6** |
| 11 | 11 | 13 | 13 | 13 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 13 | 12 | 13 | TSW | TSW | 11 | **218** | **368.2** |
| 11 | 11 | 13 | 13 | 13 | 12 | 12 | 13 | 12 | 12 | 12 | 12 | 12 | 12 | 13 | 12 | 13 | TSW | TSW | 11 | **219** | **369.8** |
| 11 | 11 | 13 | 13 | 13 | 12 | 12 | 13 | 12 | 13 | 12 | 12 | 12 | 12 | 13 | 12 | 13 | TSW | TSW | 11 | **220** | **371.4** |
| 11 | 11 | 13 | 13 | 13 | 12 | 12 | 13 | 12 | 13 | 12 | 13 | 12 | 12 | 13 | 12 | 13 | TSW | TSW | 11 | **221** | **373** |
| 11 | 11 | 13 | 13 | 13 | 13 | 12 | 13 | 12 | 13 | 12 | 13 | 12 | 12 | 13 | 12 | 13 | TSW | TSW | 11 | **222** | **374.6** |
| 11 | 11 | 13 | 13 | 13 | 13 | 12 | 13 | 12 | 13 | 12 | 13 | 12 | 12 | 13 | 13 | 13 | TSW | TSW | 11 | **223** | **376.2** |
| 11 | 11 | 13 | 13 | 13 | 13 | 13 | 13 | 12 | 13 | 12 | 13 | 12 | 12 | 13 | 13 | 13 | TSW | TSW | 11 | **224** | **377.8** |
| 11 | 11 | 13 | 13 | 13 | 13 | 13 | 13 | 12 | 13 | 12 | 13 | 12 | 13 | 13 | 13 | 13 | TSW | TSW | 11 | **225** | **379.4** |
| 11 | 11 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 12 | 13 | 12 | 13 | 13 | 13 | 13 | TSW | TSW | 11 | **226** | **381** |
| 11 | 11 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 12 | 13 | 13 | 13 | 13 | TSW | TSW | 11 | **227** | **382.6** |
| 11 | 11 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | TSW | TSW | 11 | **228** | **384.2** |
| 11 | 11 | 14 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | TSW | TSW | 11 | **229** | **385.8** |
| 11 | 11 | 14 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 14 | TSW | TSW | 11 | **230** | **387.4** |
| 11 | 11 | 14 | 14 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 14 | TSW | TSW | 11 | **231** | **389** |
| 11 | 11 | 14 | 14 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 14 | 13 | 14 | TSW | TSW | 11 | **232** | **390.6** |
| 11 | 11 | 14 | 14 | 14 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 14 | 13 | 14 | TSW | TSW | 11 | **233** | **392.2** |
| 11 | 11 | 14 | 14 | 14 | 13 | 13 | 14 | 13 | 13 | 13 | 13 | 13 | 13 | 14 | 13 | 14 | TSW | TSW | 11 | **234** | **393.8** |
| 11 | 11 | 14 | 14 | 14 | 13 | 13 | 14 | 13 | 14 | 13 | 13 | 13 | 13 | 14 | 13 | 14 | TSW | TSW | 11 | **235** | **395.4** |
| 11 | 11 | 14 | 14 | 14 | 13 | 13 | 14 | 13 | 14 | 13 | 14 | 13 | 13 | 14 | 13 | 14 | TSW | TSW | 11 | **236** | **397** |
| 11 | 11 | 14 | 14 | 14 | 14 | 13 | 14 | 13 | 14 | 13 | 14 | 13 | 13 | 14 | 13 | 14 | TSW | TSW | 11 | **237** | **398.6** |
| 11 | 11 | 14 | 14 | 14 | 14 | 13 | 14 | 13 | 14 | 13 | 14 | 13 | 13 | 14 | 14 | 14 | TSW | TSW | 11 | **238** | **400.2** |
| 11 | 11 | 14 | 14 | 14 | 14 | 14 | 14 | 13 | 14 | 13 | 14 | 13 | 13 | 14 | 14 | 14 | TSW | TSW | 11 | **239** | **401.8** |
| 11 | 11 | 14 | 14 | 14 | 14 | 14 | 14 | 13 | 14 | 13 | 14 | 13 | 14 | 14 | 14 | 14 | TSW | TSW | 11 | **240** | **403.4** |
| 11 | 11 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 13 | 14 | 13 | 14 | 14 | 14 | 14 | TSW | TSW | 11 | **241** | **405** |
| 11 | 11 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 13 | 14 | 14 | 14 | 14 | TSW | TSW | 11 | **242** | **406.6** |
| 11 | 11 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | TSW | TSW | 11 | **243** | **408.2** |
| 11 | 11 | 15 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | TSW | TSW | 11 | **244** | **409.8** |
| 11 | 11 | 15 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 15 | TSW | TSW | 11 | **245** | **411.4** |
| 11 | 11 | 15 | 15 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 15 | TSW | TSW | 11 | **246** | **413** |
| 11 | 11 | 15 | 15 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 15 | 14 | 15 | TSW | TSW | 11 | **247** | **414.6** |
| 11 | 11 | 15 | 15 | 15 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 15 | 14 | 15 | TSW | TSW | 11 | **248** | **416.2** |
| 11 | 11 | 15 | 15 | 15 | 14 | 14 | 15 | 14 | 14 | 14 | 14 | 14 | 14 | 15 | 14 | 15 | TSW | TSW | 11 | **249** | **417.8** |
| 11 | 11 | 15 | 15 | 15 | 14 | 14 | 15 | 14 | 15 | 14 | 14 | 14 | 14 | 15 | 14 | 15 | TSW | TSW | 11 | **250** | **419.4** |
| 11 | 11 | 15 | 15 | 15 | 14 | 14 | 15 | 14 | 15 | 14 | 15 | 14 | 14 | 15 | 14 | 15 | TSW | TSW | 11 | **251** | **421** |
| 11 | 11 | 15 | 15 | 15 | 15 | 14 | 15 | 14 | 15 | 14 | 15 | 14 | 14 | 15 | 14 | 15 | TSW | TSW | 11 | **252** | **422.6** |
| 11 | 11 | 15 | 15 | 15 | 15 | 14 | 15 | 14 | 15 | 14 | 15 | 14 | 14 | 15 | 15 | 15 | TSW | TSW | 11 | **253** | **424.2** |
| 11 | 11 | 15 | 15 | 15 | 15 | 15 | 15 | 14 | 15 | 14 | 15 | 14 | 14 | 15 | 15 | 15 | TSW | TSW | 11 | **254** | **425.8** |
| 11 | 11 | 15 | 15 | 15 | 15 | 15 | 15 | 14 | 15 | 14 | 15 | 14 | 15 | 15 | 15 | 15 | TSW | TSW | 11 | **255** | **427.4** |
| 11 | 11 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 14 | 15 | 14 | 15 | 15 | 15 | 15 | TSW | TSW | 11 | **256** | **429** |
| 11 | 11 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 14 | 15 | 15 | 15 | 15 | TSW | TSW | 11 | **257** | **430.6** |
| 11 | 11 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | TSW | TSW | 11 | **258** | **432.2** |
| 11 | 11 | 16 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | TSW | TSW | 11 | **259** | **433.8** |
| 11 | 11 | 16 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 16 | TSW | TSW | 11 | **260** | **435.4** |
| 11 | 11 | 16 | 16 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 16 | TSW | TSW | 11 | **261** | **437** |
| 11 | 11 | 16 | 16 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 16 | 15 | 16 | TSW | TSW | 11 | **262** | **438.6** |
| 11 | 11 | 16 | 16 | 16 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 16 | 15 | 16 | TSW | TSW | 11 | **263** | **440.2** |
| 11 | 11 | 16 | 16 | 16 | 15 | 15 | 16 | 15 | 15 | 15 | 15 | 15 | 15 | 16 | 15 | 16 | TSW | TSW | 11 | **264** | **441.8** |
| 11 | 11 | 16 | 16 | 16 | 15 | 15 | 16 | 15 | 16 | 15 | 15 | 15 | 15 | 16 | 15 | 16 | TSW | TSW | 11 | **265** | **443.4** |
| 11 | 11 | 16 | 16 | 16 | 15 | 15 | 16 | 15 | 16 | 15 | 16 | 15 | 15 | 16 | 15 | 16 | TSW | TSW | 11 | **266** | **445** |
| 11 | 11 | 16 | 16 | 16 | 16 | 15 | 16 | 15 | 16 | 15 | 16 | 15 | 15 | 16 | 15 | 16 | TSW | TSW | 11 | **267** | **446.6** |
| 11 | 11 | 16 | 16 | 16 | 16 | 15 | 16 | 15 | 16 | 15 | 16 | 15 | 15 | 16 | 16 | 16 | TSW | TSW | 11 | **268** | **448.2** |
| 11 | 11 | 16 | 16 | 16 | 16 | 16 | 16 | 15 | 16 | 15 | 16 | 15 | 15 | 16 | 16 | 16 | TSW | TSW | 11 | **269** | **449.8** |
| 11 | 11 | 16 | 16 | 16 | 16 | 16 | 16 | 15 | 16 | 15 | 16 | 15 | 16 | 16 | 16 | 16 | TSW | TSW | 11 | **270** | **451.4** |
| 11 | 11 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 15 | 16 | 15 | 16 | 16 | 16 | 16 | TSW | TSW | 11 | **271** | **453** |
| 11 | 11 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 15 | 16 | 16 | 16 | 16 | TSW | TSW | 11 | **272** | **454.6** |
| 11 | 11 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | TSW | TSW | 11 | **273** | **456.2** |
| 11 | 11 | 17 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | TSW | TSW | 11 | **274** | **457.8** |
| 11 | 11 | 17 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 17 | TSW | TSW | 11 | **275** | **459.4** |
| 11 | 11 | 17 | 17 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 17 | TSW | TSW | 11 | **276** | **461** |
| 11 | 11 | 17 | 17 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 17 | 16 | 17 | TSW | TSW | 11 | **277** | **462.6** |
| 11 | 11 | 17 | 17 | 17 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 17 | 16 | 17 | TSW | TSW | 11 | **278** | **464.2** |
| 11 | 11 | 17 | 17 | 17 | 16 | 16 | 17 | 16 | 16 | 16 | 16 | 16 | 16 | 17 | 16 | 17 | TSW | TSW | 11 | **279** | **465.8** |
| 11 | 11 | 17 | 17 | 17 | 16 | 16 | 17 | 16 | 17 | 16 | 16 | 16 | 16 | 17 | 16 | 17 | TSW | TSW | 11 | **280** | **467.4** |
| 11 | 11 | 17 | 17 | 17 | 16 | 16 | 17 | 16 | 17 | 16 | 17 | 16 | 16 | 17 | 16 | 17 | TSW | TSW | 11 | **281** | **469** |
| 11 | 11 | 17 | 17 | 17 | 17 | 16 | 17 | 16 | 17 | 16 | 17 | 16 | 16 | 17 | 16 | 17 | TSW | TSW | 11 | **282** | **470.6** |
| 11 | 11 | 17 | 17 | 17 | 17 | 16 | 17 | 16 | 17 | 16 | 17 | 16 | 16 | 17 | 17 | 17 | TSW | TSW | 11 | **283** | **472.2** |
| 11 | 11 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 17 | 16 | 17 | 16 | 16 | 17 | 17 | 17 | TSW | TSW | 11 | **284** | **473.8** |
| 11 | 11 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 17 | 16 | 17 | 16 | 17 | 17 | 17 | 17 | TSW | TSW | 11 | **285** | **475.4** |
| 11 | 11 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 17 | 16 | 17 | 17 | 17 | 17 | TSW | TSW | 11 | **286** | **477** |
| 11 | 11 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 17 | 17 | 17 | 17 | TSW | TSW | 11 | **287** | **478.6** |
| 11 | 11 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | TSW | TSW | 11 | **288** | **480.2** |
| 11 | 11 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | TSW | TSW | 11 | **289** | **481.8** |
| 11 | 11 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | TSW | TSW | 11 | **290** | **483.4** |
| 11 | 11 | 18 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | TSW | TSW | 11 | **291** | **485** |
| 11 | 11 | 18 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 17 | 18 | TSW | TSW | 11 | **292** | **486.6** |
| 11 | 11 | 18 | 18 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 17 | 18 | TSW | TSW | 11 | **293** | **488.2** |
| 11 | 11 | 18 | 18 | 18 | 17 | 17 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 17 | 18 | TSW | TSW | 11 | **294** | **489.8** |
| 11 | 11 | 18 | 18 | 18 | 17 | 17 | 18 | 17 | 18 | 17 | 17 | 17 | 17 | 18 | 17 | 18 | TSW | TSW | 11 | **295** | **491.4** |
| 11 | 11 | 18 | 18 | 18 | 17 | 17 | 18 | 17 | 18 | 17 | 18 | 17 | 17 | 18 | 17 | 18 | TSW | TSW | 11 | **296** | **493** |
| 11 | 11 | 18 | 18 | 18 | 18 | 17 | 18 | 17 | 18 | 17 | 18 | 17 | 17 | 18 | 17 | 18 | TSW | TSW | 11 | **297** | **494.6** |
| 11 | 11 | 18 | 18 | 18 | 18 | 17 | 18 | 17 | 18 | 17 | 18 | 17 | 17 | 18 | 18 | 18 | TSW | TSW | 11 | **298** | **496.2** |
| 11 | 11 | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 18 | 17 | 18 | 17 | 17 | 18 | 18 | 18 | TSW | TSW | 11 | **299** | **497.8** |
| 11 | 11 | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 18 | 17 | 18 | 17 | 18 | 18 | 18 | 18 | TSW | TSW | 11 | **300** | **499.4** |
| 11 | 11 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 18 | 17 | 18 | 18 | 18 | 18 | TSW | TSW | 11 | **301** | **501** |
| 11 | 11 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 18 | 18 | 18 | 18 | TSW | TSW | 11 | **302** | **502.6** |
| 11 | 11 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | TSW | TSW | 11 | **303** | **504.2** |
| 11 | 11 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | TSW | TSW | 11 | **304** | **505.8** |
| 11 | 11 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 19 | TSW | TSW | 11 | **305** | **507.4** |
| 11 | 11 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 19 | TSW | TSW | 11 | **306** | **509** |
| 11 | 11 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 18 | 19 | TSW | TSW | 11 | **307** | **510.6** |
| 11 | 11 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 18 | 19 | TSW | TSW | 11 | **308** | **512.2** |
| 11 | 11 | 19 | 19 | 19 | 18 | 18 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 18 | 19 | TSW | TSW | 11 | **309** | **513.8** |
| 11 | 11 | 19 | 19 | 19 | 18 | 18 | 19 | 18 | 19 | 18 | 18 | 18 | 18 | 19 | 18 | 19 | TSW | TSW | 11 | **310** | **515.4** |
| 11 | 11 | 19 | 19 | 19 | 18 | 18 | 19 | 18 | 19 | 18 | 19 | 18 | 18 | 19 | 18 | 19 | TSW | TSW | 11 | **311** | **517** |
| 11 | 11 | 19 | 19 | 19 | 19 | 18 | 19 | 18 | 19 | 18 | 19 | 18 | 18 | 19 | 18 | 19 | TSW | TSW | 11 | **312** | **518.6** |
| 11 | 11 | 19 | 19 | 19 | 19 | 18 | 19 | 18 | 19 | 18 | 19 | 18 | 18 | 19 | 19 | 19 | TSW | TSW | 11 | **313** | **520.2** |
| 11 | 11 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 19 | 18 | 19 | 18 | 18 | 19 | 19 | 19 | TSW | TSW | 11 | **314** | **521.8** |
| 11 | 11 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 19 | 18 | 19 | 18 | 19 | 19 | 19 | 19 | TSW | TSW | 11 | **315** | **523.4** |
| 11 | 11 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 19 | 18 | 19 | 19 | 19 | 19 | TSW | TSW | 11 | **316** | **525** |
| 11 | 11 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 19 | 19 | 19 | 19 | TSW | TSW | 11 | **317** | **526.6** |
| 11 | 11 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | TSW | TSW | 11 | **318** | **528.2** |
| 11 | 11 | 20 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | TSW | TSW | 11 | **319** | **529.8** |
| 11 | 11 | 20 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 20 | TSW | TSW | 11 | **320** | **531.4** |
| 11 | 11 | 20 | 20 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 20 | TSW | TSW | 11 | **321** | **533** |
| 11 | 11 | 20 | 20 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 19 | 20 | TSW | TSW | 11 | **322** | **534.6** |
| 11 | 11 | 20 | 20 | 20 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 19 | 20 | TSW | TSW | 11 | **323** | **536.2** |
| 11 | 11 | 20 | 20 | 20 | 19 | 19 | 20 | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 19 | 20 | TSW | TSW | 11 | **324** | **537.8** |
| 11 | 11 | 20 | 20 | 20 | 19 | 19 | 20 | 19 | 20 | 19 | 19 | 19 | 19 | 20 | 19 | 20 | TSW | TSW | 11 | **325** | **539.4** |
| 11 | 11 | 20 | 20 | 20 | 19 | 19 | 20 | 19 | 20 | 19 | 20 | 19 | 19 | 20 | 19 | 20 | TSW | TSW | 11 | **326** | **541** |
| 11 | 11 | 20 | 20 | 20 | 20 | 19 | 20 | 19 | 20 | 19 | 20 | 19 | 19 | 20 | 19 | 20 | TSW | TSW | 11 | **327** | **542.6** |
| 11 | 11 | 20 | 20 | 20 | 20 | 19 | 20 | 19 | 20 | 19 | 20 | 19 | 19 | 20 | 20 | 20 | TSW | TSW | 11 | **328** | **544.2** |
| 11 | 11 | 20 | 20 | 20 | 20 | 20 | 20 | 19 | 20 | 19 | 20 | 19 | 19 | 20 | 20 | 20 | TSW | TSW | 11 | **329** | **545.8** |
| 11 | 11 | 20 | 20 | 20 | 20 | 20 | 20 | 19 | 20 | 19 | 20 | 19 | 20 | 20 | 20 | 20 | TSW | TSW | 11 | **330** | **547.4** |
| 11 | 11 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 19 | 20 | 19 | 20 | 20 | 20 | 20 | TSW | TSW | 11 | **331** | **549** |
| 11 | 11 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 19 | 20 | 20 | 20 | 20 | TSW | TSW | 11 | **332** | **550.6** |
| 11 | 11 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | TSW | TSW | 11 | **333** | **552.2** |
| 11 | 11 | 21 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | TSW | TSW | 11 | **334** | **553.8** |
| 11 | 11 | 21 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 21 | TSW | TSW | 11 | **335** | **555.4** |
| 11 | 11 | 21 | 21 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 21 | TSW | TSW | 11 | **336** | **557** |
| 11 | 11 | 21 | 21 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 20 | 21 | TSW | TSW | 11 | **337** | **558.6** |
| 11 | 11 | 21 | 21 | 21 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 20 | 21 | TSW | TSW | 11 | **338** | **560.2** |
| 11 | 11 | 21 | 21 | 21 | 20 | 20 | 21 | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 20 | 21 | TSW | TSW | 11 | **339** | **561.8** |
| 11 | 11 | 21 | 21 | 21 | 20 | 20 | 21 | 20 | 21 | 20 | 20 | 20 | 20 | 21 | 20 | 21 | TSW | TSW | 11 | **340** | **563.4** |
| 11 | 11 | 21 | 21 | 21 | 20 | 20 | 21 | 20 | 21 | 20 | 21 | 20 | 20 | 21 | 20 | 21 | TSW | TSW | 11 | **341** | **565** |
| 11 | 11 | 21 | 21 | 21 | 21 | 20 | 21 | 20 | 21 | 20 | 21 | 20 | 20 | 21 | 20 | 21 | TSW | TSW | 11 | **342** | **566.6** |
| 11 | 11 | 21 | 21 | 21 | 21 | 20 | 21 | 20 | 21 | 20 | 21 | 20 | 20 | 21 | 21 | 21 | TSW | TSW | 11 | **343** | **568.2** |
| 11 | 11 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 21 | 20 | 21 | 20 | 20 | 21 | 21 | 21 | TSW | TSW | 11 | **344** | **569.8** |
| 11 | 11 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 21 | 20 | 21 | 20 | 21 | 21 | 21 | 21 | TSW | TSW | 11 | **345** | **571.4** |
| 11 | 11 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 21 | 20 | 21 | 21 | 21 | 21 | TSW | TSW | 11 | **346** | **573** |
| 11 | 11 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 21 | 21 | 21 | 21 | TSW | TSW | 11 | **347** | **574.6** |
| 11 | 11 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | TSW | TSW | 11 | **348** | **576.2** |
| 11 | 11 | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | TSW | TSW | 11 | **349** | **577.8** |
| 11 | 11 | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 22 | TSW | TSW | 11 | **350** | **579.4** |
| 11 | 11 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 22 | TSW | TSW | 11 | **351** | **581** |
| 11 | 11 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 22 | 21 | 22 | TSW | TSW | 11 | **352** | **582.6** |
| 11 | 11 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 22 | 21 | 22 | TSW | TSW | 11 | **353** | **584.2** |
| 11 | 11 | 22 | 22 | 22 | 21 | 21 | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 22 | 21 | 22 | TSW | TSW | 11 | **354** | **585.8** |
| 11 | 11 | 22 | 22 | 22 | 21 | 21 | 22 | 21 | 22 | 21 | 21 | 21 | 21 | 22 | 21 | 22 | TSW | TSW | 11 | **355** | **587.4** |
| 11 | 11 | 22 | 22 | 22 | 21 | 21 | 22 | 21 | 22 | 21 | 22 | 21 | 21 | 22 | 21 | 22 | TSW | TSW | 11 | **356** | **589** |
| 11 | 11 | 22 | 22 | 22 | 22 | 21 | 22 | 21 | 22 | 21 | 22 | 21 | 21 | 22 | 21 | 22 | TSW | TSW | 11 | **357** | **590.6** |
| 11 | 11 | 22 | 22 | 22 | 22 | 21 | 22 | 21 | 22 | 21 | 22 | 21 | 21 | 22 | 22 | 22 | TSW | TSW | 11 | **358** | **592.2** |
| 11 | 11 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 22 | 21 | 22 | 21 | 21 | 22 | 22 | 22 | TSW | TSW | 11 | **359** | **593.8** |
| 11 | 11 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 22 | 21 | 22 | 21 | 22 | 22 | 22 | 22 | TSW | TSW | 11 | **360** | **595.4** |
| 11 | 11 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 22 | 21 | 22 | 22 | 22 | 22 | TSW | TSW | 11 | **361** | **597** |
| 11 | 11 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 22 | 22 | 22 | 22 | TSW | TSW | 11 | **362** | **598.6** |
| 11 | 11 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | TSW | TSW | 11 | **363** | **600.2** |

Table JDA-9. [*pg 1 of 8*] John Day Dam Spill Pattern with No TSWs (Bays 18-19 Closed).

| **JDA Spill Patterns with No TSWs - # Gate Stops per Spillbay** | | | | | | | | | | | | | | | | | | | | **Total** | **Spill** [[10]](#footnote-10) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **1 [[11]](#footnote-11)** | **2** | **3** | **4** | **5** | **6** | **7** | **8** | **9** | **10** | **11** | **12** | **13** | **14** | **15** | **16** | **17** | **18** | **19** | **20** | **Stops (#)** | **(kcfs)** |
|  | 3 | 2 | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  | CLOSE | CLOSE |  | **6** | **9.6** |
|  | 3 | 2 | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  | CLOSE | CLOSE |  | **7** | **11.2** |
|  | 3 | 3 | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  | CLOSE | CLOSE |  | **8** | **12.8** |
|  | 3 | 3 | 2 | 1 |  |  |  |  |  |  |  |  |  |  |  |  | CLOSE | CLOSE |  | **9** | **14.4** |
|  | 3 | 3 | 2 | 2 |  |  |  |  |  |  |  |  |  |  |  |  | CLOSE | CLOSE |  | **10** | **16.0** |
|  | 3 | 3 | 2 | 2 | 1 |  |  |  |  |  |  |  |  |  |  |  | CLOSE | CLOSE |  | **11** | **17.6** |
|  | 3 | 3 | 2 | 2 | 2 |  |  |  |  |  |  |  |  |  |  |  | CLOSE | CLOSE |  | **12** | **19.2** |
|  | 3 | 3 | 2 | 2 | 2 | 1 |  |  |  |  |  |  |  |  |  |  | CLOSE | CLOSE |  | **13** | **20.8** |
|  | 3 | 3 | 2 | 2 | 2 | 2 |  |  |  |  |  |  |  |  |  |  | CLOSE | CLOSE |  | **14** | **22.4** |
|  | 3 | 3 | 2 | 2 | 2 | 2 | 1 |  |  |  |  |  |  |  |  |  | CLOSE | CLOSE |  | **15** | **24.0** |
|  | 3 | 3 | 3 | 2 | 2 | 2 | 1 |  |  |  |  |  |  |  |  |  | CLOSE | CLOSE |  | **16** | **25.6** |
|  | 3 | 3 | 3 | 2 | 2 | 2 | 2 |  |  |  |  |  |  |  |  |  | CLOSE | CLOSE |  | **17** | **27.2** |
|  | 3 | 3 | 3 | 2 | 2 | 2 | 2 | 1 |  |  |  |  |  |  |  |  | CLOSE | CLOSE |  | **18** | **28.8** |
|  | 3 | 3 | 3 | 3 | 2 | 2 | 2 | 1 |  |  |  |  |  |  |  |  | CLOSE | CLOSE |  | **19** | **30.4** |
|  | 3 | 3 | 3 | 3 | 3 | 2 | 2 | 1 |  |  |  |  |  |  |  |  | CLOSE | CLOSE |  | **20** | **32.0** |
|  | 3 | 3 | 3 | 3 | 3 | 2 | 2 | 2 |  |  |  |  |  |  |  |  | CLOSE | CLOSE |  | **21** | **33.6** |
|  | 3 | 3 | 3 | 3 | 3 | 2 | 2 | 2 | 1 |  |  |  |  |  |  |  | CLOSE | CLOSE |  | **22** | **35.2** |
|  | 3 | 3 | 3 | 3 | 3 | 2 | 2 | 2 | 2 |  |  |  |  |  |  |  | CLOSE | CLOSE |  | **23** | **36.8** |
|  | 3 | 3 | 3 | 3 | 3 | 2 | 2 | 2 | 2 | 1 |  |  |  |  |  |  | CLOSE | CLOSE |  | **24** | **38.4** |
|  | 3 | 3 | 3 | 3 | 3 | 2 | 2 | 2 | 2 | 2 |  |  |  |  |  |  | CLOSE | CLOSE |  | **25** | **40.0** |
|  | 3 | 3 | 3 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 1 |  |  |  |  |  | CLOSE | CLOSE |  | **26** | **41.6** |
|  | 3 | 3 | 3 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 2 |  |  |  |  |  | CLOSE | CLOSE |  | **27** | **43.2** |
|  | 3 | 3 | 3 | 3 | 3 | 3 | 2 | 2 | 2 | 2 | 2 |  |  |  |  |  | CLOSE | CLOSE |  | **28** | **44.8** |
|  | 3 | 3 | 3 | 3 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 1 |  |  |  |  | CLOSE | CLOSE |  | **29** | **46.4** |
|  | 3 | 3 | 3 | 3 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 2 |  |  |  |  | CLOSE | CLOSE |  | **30** | **48.0** |
|  | 3 | 3 | 3 | 3 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 1 |  |  |  | CLOSE | CLOSE |  | **31** | **49.6** |
|  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 1 |  |  |  | CLOSE | CLOSE |  | **32** | **51.2** |
|  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 2 |  |  |  | CLOSE | CLOSE |  | **33** | **52.8** |
|  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 1 |  |  | CLOSE | CLOSE |  | **34** | **54.4** |
|  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  | CLOSE | CLOSE |  | **35** | **56.0** |
|  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 |  | CLOSE | CLOSE |  | **36** | **57.6** |
|  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | CLOSE | CLOSE |  | **37** | **59.2** |
|  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | CLOSE | CLOSE |  | **38** | **60.8** |
|  | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | CLOSE | CLOSE |  | **39** | **62.4** |
|  | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | CLOSE | CLOSE |  | **40** | **64.0** |
|  | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | CLOSE | CLOSE |  | **41** | **65.6** |
|  | 4 | 4 | 4 | 4 | 3 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | CLOSE | CLOSE |  | **42** | **67.2** |
|  | 4 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | CLOSE | CLOSE |  | **43** | **68.8** |
|  | 4 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | CLOSE | CLOSE |  | **44** | **70.4** |
|  | 4 | 4 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | CLOSE | CLOSE |  | **45** | **72.0** |
|  | 4 | 5 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | CLOSE | CLOSE |  | **46** | **73.6** |
|  | 4 | 5 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | CLOSE | CLOSE |  | **47** | **75.2** |
|  | 4 | 5 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | CLOSE | CLOSE |  | **48** | **76.8** |
|  | 4 | 5 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | CLOSE | CLOSE |  | **49** | **78.4** |
|  | 4 | 5 | 5 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | CLOSE | CLOSE |  | **50** | **80.0** |
|  | 4 | 5 | 5 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | CLOSE | CLOSE |  | **51** | **81.6** |
|  | 4 | 5 | 5 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 2 | 2 | 2 | 2 | CLOSE | CLOSE |  | **52** | **83.2** |
|  | 4 | 5 | 5 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 2 | 2 | 2 | CLOSE | CLOSE |  | **53** | **84.8** |
|  | 4 | 5 | 5 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 2 | 2 | CLOSE | CLOSE |  | **54** | **86.4** |
|  | 4 | 5 | 5 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 2 | CLOSE | CLOSE |  | **55** | **88.0** |
|  | 4 | 5 | 5 | 4 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 2 | CLOSE | CLOSE |  | **56** | **89.6** |
|  | 4 | 5 | 5 | 4 | 4 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 2 | CLOSE | CLOSE |  | **57** | **91.2** |
|  | 4 | 5 | 5 | 5 | 4 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 2 | CLOSE | CLOSE |  | **58** | **92.8** |
|  | 4 | 5 | 5 | 5 | 4 | 4 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 2 | CLOSE | CLOSE |  | **59** | **94.4** |
|  | 4 | 5 | 5 | 5 | 4 | 4 | 4 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 2 | CLOSE | CLOSE |  | **60** | **96.0** |
|  | 4 | 5 | 5 | 5 | 4 | 4 | 4 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | CLOSE | CLOSE |  | **61** | **97.6** |
|  | 4 | 5 | 5 | 5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | CLOSE | CLOSE |  | **62** | **99.2** |
|  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 3 | 4 | 4 | 4 | 4 | CLOSE | CLOSE |  | **63** | **100.8** |
|  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | CLOSE | CLOSE |  | **64** | **102.4** |
|  | 4 | 5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | CLOSE | CLOSE |  | **65** | **104.0** |
|  | 4 | 5 | 5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | CLOSE | CLOSE |  | **66** | **105.6** |
|  | 4 | 5 | 5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | CLOSE | CLOSE |  | **67** | **107.2** |
|  | 4 | 5 | 5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 4 | 5 | CLOSE | CLOSE |  | **68** | **108.8** |
|  | 4 | 5 | 5 | 5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 4 | 5 | CLOSE | CLOSE |  | **69** | **110.4** |
|  | 4 | 5 | 5 | 5 | 4 | 4 | 5 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 4 | 5 | CLOSE | CLOSE |  | **70** | **112.0** |
|  | 4 | 5 | 5 | 5 | 4 | 4 | 5 | 4 | 5 | 4 | 4 | 4 | 4 | 5 | 4 | 5 | CLOSE | CLOSE |  | **71** | **113.6** |
|  | 4 | 5 | 5 | 5 | 4 | 4 | 5 | 4 | 5 | 4 | 5 | 4 | 4 | 5 | 4 | 5 | CLOSE | CLOSE |  | **72** | **115.2** |
|  | 4 | 5 | 5 | 5 | 5 | 4 | 5 | 4 | 5 | 4 | 5 | 4 | 4 | 5 | 4 | 5 | CLOSE | CLOSE |  | **73** | **116.8** |
|  | 4 | 5 | 5 | 5 | 5 | 4 | 5 | 4 | 5 | 4 | 5 | 4 | 4 | 5 | 5 | 5 | CLOSE | CLOSE |  | **74** | **118.4** |
|  | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 4 | 5 | 4 | 5 | 4 | 4 | 5 | 5 | 5 | CLOSE | CLOSE |  | **75** | **120.0** |
|  | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 4 | 5 | 4 | 5 | 4 | 5 | 5 | 5 | 5 | CLOSE | CLOSE |  | **76** | **121.6** |
|  | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 4 | 5 | 4 | 5 | 5 | 5 | 5 | CLOSE | CLOSE |  | **77** | **123.2** |
|  | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 4 | 5 | 5 | 5 | 5 | CLOSE | CLOSE |  | **78** | **124.8** |
|  | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | CLOSE | CLOSE |  | **79** | **126.4** |
|  | 4 | 6 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | CLOSE | CLOSE |  | **80** | **128.0** |
|  | 4 | 6 | 6 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | CLOSE | CLOSE |  | **81** | **129.6** |
|  | 4 | 6 | 6 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 6 | CLOSE | CLOSE |  | **82** | **131.2** |
|  | 4 | 6 | 6 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 5 | 6 | CLOSE | CLOSE |  | **83** | **132.8** |
|  | 4 | 6 | 6 | 6 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 5 | 6 | CLOSE | CLOSE |  | **84** | **134.4** |
|  | 4 | 6 | 6 | 6 | 5 | 5 | 6 | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 5 | 6 | CLOSE | CLOSE |  | **85** | **136.0** |
|  | 4 | 6 | 6 | 6 | 5 | 5 | 6 | 5 | 6 | 5 | 5 | 5 | 5 | 6 | 5 | 6 | CLOSE | CLOSE |  | **86** | **137.6** |
|  | 4 | 6 | 6 | 6 | 5 | 5 | 6 | 5 | 6 | 5 | 6 | 5 | 5 | 6 | 5 | 6 | CLOSE | CLOSE |  | **87** | **139.2** |
|  | 4 | 6 | 6 | 6 | 6 | 5 | 6 | 5 | 6 | 5 | 6 | 5 | 5 | 6 | 5 | 6 | CLOSE | CLOSE |  | **88** | **140.8** |
|  | 4 | 6 | 6 | 6 | 6 | 5 | 6 | 5 | 6 | 5 | 6 | 5 | 5 | 6 | 6 | 6 | CLOSE | CLOSE |  | **89** | **142.4** |
|  | 4 | 6 | 6 | 6 | 6 | 6 | 6 | 5 | 6 | 5 | 6 | 5 | 5 | 6 | 6 | 6 | CLOSE | CLOSE |  | **90** | **144.0** |
|  | 4 | 6 | 6 | 6 | 6 | 6 | 6 | 5 | 6 | 5 | 6 | 5 | 6 | 6 | 6 | 6 | CLOSE | CLOSE |  | **91** | **145.6** |
|  | 4 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 5 | 6 | 5 | 6 | 6 | 6 | 6 | CLOSE | CLOSE |  | **92** | **147.2** |
|  | 4 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 5 | 6 | 6 | 6 | 6 | CLOSE | CLOSE |  | **93** | **148.8** |
|  | 4 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | CLOSE | CLOSE |  | **94** | **150.4** |
|  | 4 | 6 | 7 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | CLOSE | CLOSE |  | **95** | **152.0** |
|  | 4 | 6 | 7 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 7 | CLOSE | CLOSE |  | **96** | **153.6** |
|  | 4 | 6 | 7 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 6 | 7 | CLOSE | CLOSE |  | **97** | **155.2** |
|  | 4 | 6 | 7 | 7 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 6 | 7 | CLOSE | CLOSE |  | **98** | **156.8** |
|  | 4 | 6 | 7 | 7 | 6 | 6 | 7 | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 6 | 7 | CLOSE | CLOSE |  | **99** | **158.4** |
|  | 4 | 6 | 7 | 7 | 6 | 6 | 7 | 6 | 7 | 6 | 6 | 6 | 6 | 7 | 6 | 7 | CLOSE | CLOSE |  | **100** | **160.0** |
|  | 4 | 6 | 7 | 7 | 6 | 6 | 7 | 6 | 7 | 6 | 7 | 6 | 6 | 7 | 6 | 7 | CLOSE | CLOSE |  | **101** | **161.6** |
|  | 4 | 6 | 7 | 7 | 7 | 6 | 7 | 6 | 7 | 6 | 7 | 6 | 6 | 7 | 6 | 7 | CLOSE | CLOSE |  | **102** | **163.2** |
|  | 4 | 6 | 7 | 7 | 7 | 6 | 7 | 6 | 7 | 6 | 7 | 6 | 6 | 7 | 7 | 7 | CLOSE | CLOSE |  | **103** | **164.8** |
|  | 4 | 6 | 7 | 7 | 7 | 7 | 7 | 6 | 7 | 6 | 7 | 6 | 6 | 7 | 7 | 7 | CLOSE | CLOSE |  | **104** | **166.4** |
|  | 4 | 6 | 7 | 7 | 7 | 7 | 7 | 6 | 7 | 6 | 7 | 6 | 7 | 7 | 7 | 7 | CLOSE | CLOSE |  | **105** | **168.0** |
|  | 4 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 6 | 7 | 6 | 7 | 7 | 7 | 7 | CLOSE | CLOSE |  | **106** | **169.6** |
|  | 4 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 6 | 7 | 7 | 7 | 7 | CLOSE | CLOSE |  | **107** | **171.2** |
|  | 4 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | CLOSE | CLOSE |  | **108** | **172.8** |
|  | 4 | 6 | 8 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | CLOSE | CLOSE |  | **109** | **174.4** |
|  | 4 | 6 | 8 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 8 | CLOSE | CLOSE |  | **110** | **176.0** |
|  | 4 | 6 | 8 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 8 | 7 | 8 | CLOSE | CLOSE |  | **111** | **177.6** |
|  | 4 | 6 | 8 | 8 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 8 | 7 | 8 | CLOSE | CLOSE |  | **112** | **179.2** |
|  | 4 | 6 | 8 | 8 | 7 | 7 | 8 | 7 | 7 | 7 | 7 | 7 | 7 | 8 | 7 | 8 | CLOSE | CLOSE |  | **113** | **180.8** |
|  | 4 | 6 | 8 | 8 | 7 | 7 | 8 | 7 | 8 | 7 | 7 | 7 | 7 | 8 | 7 | 8 | CLOSE | CLOSE |  | **114** | **182.4** |
|  | 4 | 6 | 8 | 8 | 7 | 7 | 8 | 7 | 8 | 7 | 8 | 7 | 7 | 8 | 7 | 8 | CLOSE | CLOSE |  | **115** | **184.0** |
|  | 4 | 6 | 8 | 8 | 8 | 7 | 8 | 7 | 8 | 7 | 8 | 7 | 7 | 8 | 7 | 8 | CLOSE | CLOSE |  | **116** | **185.6** |
|  | 4 | 6 | 8 | 8 | 8 | 7 | 8 | 7 | 8 | 7 | 8 | 7 | 7 | 8 | 8 | 8 | CLOSE | CLOSE |  | **117** | **187.2** |
|  | 4 | 6 | 8 | 8 | 8 | 8 | 8 | 7 | 8 | 7 | 8 | 7 | 7 | 8 | 8 | 8 | CLOSE | CLOSE |  | **118** | **188.8** |
|  | 4 | 6 | 8 | 8 | 8 | 8 | 8 | 7 | 8 | 7 | 8 | 7 | 8 | 8 | 8 | 8 | CLOSE | CLOSE |  | **119** | **190.4** |
|  | 4 | 6 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 7 | 8 | 7 | 8 | 8 | 8 | 8 | CLOSE | CLOSE |  | **120** | **192.0** |
|  | 4 | 6 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 7 | 8 | 8 | 8 | 8 | CLOSE | CLOSE |  | **121** | **193.6** |
|  | 4 | 6 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | CLOSE | CLOSE |  | **122** | **195.2** |
|  | 4 | 6 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 9 | CLOSE | CLOSE |  | **123** | **196.8** |
|  | 4 | 6 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 9 | 8 | 9 | CLOSE | CLOSE |  | **124** | **198.4** |
|  | 4 | 6 | 8 | 9 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 9 | 8 | 9 | CLOSE | CLOSE |  | **125** | **200.0** |
|  | 4 | 6 | 8 | 9 | 8 | 8 | 9 | 8 | 8 | 8 | 8 | 8 | 8 | 9 | 8 | 9 | CLOSE | CLOSE |  | **126** | **201.6** |
|  | 4 | 6 | 8 | 9 | 8 | 8 | 9 | 8 | 9 | 8 | 8 | 8 | 8 | 9 | 8 | 9 | CLOSE | CLOSE |  | **127** | **203.2** |
|  | 4 | 6 | 8 | 9 | 8 | 8 | 9 | 8 | 9 | 8 | 9 | 8 | 8 | 9 | 8 | 9 | CLOSE | CLOSE |  | **128** | **204.8** |
|  | 4 | 6 | 8 | 9 | 9 | 8 | 9 | 8 | 9 | 8 | 9 | 8 | 8 | 9 | 8 | 9 | CLOSE | CLOSE |  | **129** | **206.4** |
|  | 4 | 6 | 8 | 9 | 9 | 8 | 9 | 8 | 9 | 8 | 9 | 8 | 8 | 9 | 9 | 9 | CLOSE | CLOSE |  | **130** | **208.0** |
|  | 4 | 6 | 8 | 9 | 9 | 9 | 9 | 8 | 9 | 8 | 9 | 8 | 8 | 9 | 9 | 9 | CLOSE | CLOSE |  | **131** | **209.6** |
|  | 4 | 6 | 8 | 9 | 9 | 9 | 9 | 8 | 9 | 8 | 9 | 8 | 9 | 9 | 9 | 9 | CLOSE | CLOSE |  | **132** | **211.2** |
|  | 4 | 6 | 8 | 9 | 9 | 9 | 9 | 9 | 9 | 8 | 9 | 8 | 9 | 9 | 9 | 9 | CLOSE | CLOSE |  | **133** | **212.8** |
|  | 4 | 6 | 8 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 8 | 9 | 9 | 9 | 9 | CLOSE | CLOSE |  | **134** | **214.4** |
|  | 4 | 6 | 8 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | CLOSE | CLOSE |  | **135** | **216.0** |
|  | 4 | 6 | 8 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 10 | CLOSE | CLOSE |  | **136** | **217.6** |
|  | 4 | 6 | 8 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 10 | 9 | 10 | CLOSE | CLOSE |  | **137** | **219.2** |
|  | 4 | 6 | 8 | 10 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 10 | 9 | 10 | CLOSE | CLOSE |  | **138** | **220.8** |
|  | 4 | 6 | 8 | 10 | 9 | 9 | 10 | 9 | 9 | 9 | 9 | 9 | 9 | 10 | 9 | 10 | CLOSE | CLOSE |  | **139** | **222.4** |
|  | 4 | 6 | 8 | 10 | 9 | 9 | 10 | 9 | 10 | 9 | 9 | 9 | 9 | 10 | 9 | 10 | CLOSE | CLOSE |  | **140** | **224.0** |
|  | 4 | 6 | 8 | 10 | 9 | 9 | 10 | 9 | 10 | 9 | 10 | 9 | 9 | 10 | 9 | 10 | CLOSE | CLOSE |  | **141** | **225.6** |
|  | 4 | 6 | 8 | 10 | 10 | 9 | 10 | 9 | 10 | 9 | 10 | 9 | 9 | 10 | 9 | 10 | CLOSE | CLOSE |  | **142** | **227.2** |
|  | 4 | 6 | 8 | 10 | 10 | 9 | 10 | 9 | 10 | 9 | 10 | 9 | 9 | 10 | 10 | 10 | CLOSE | CLOSE |  | **143** | **228.8** |
|  | 4 | 6 | 8 | 10 | 10 | 10 | 10 | 9 | 10 | 9 | 10 | 9 | 9 | 10 | 10 | 10 | CLOSE | CLOSE |  | **144** | **230.4** |
|  | 4 | 6 | 8 | 10 | 10 | 10 | 10 | 9 | 10 | 9 | 10 | 9 | 10 | 10 | 10 | 10 | CLOSE | CLOSE |  | **145** | **232.0** |
|  | 4 | 6 | 8 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 10 | 9 | 10 | 10 | 10 | 10 | CLOSE | CLOSE |  | **146** | **233.6** |
|  | 4 | 6 | 8 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 10 | 10 | 10 | 10 | CLOSE | CLOSE |  | **147** | **235.2** |
|  | 4 | 6 | 8 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | CLOSE | CLOSE |  | **148** | **236.8** |
|  | 4 | 6 | 8 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 11 | CLOSE | CLOSE |  | **149** | **238.4** |
|  | 4 | 6 | 8 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 11 | 10 | 11 | CLOSE | CLOSE |  | **150** | **240.0** |
|  | 4 | 6 | 8 | 10 | 10 | 10 | 11 | 10 | 10 | 10 | 10 | 10 | 10 | 11 | 10 | 11 | CLOSE | CLOSE |  | **151** | **241.6** |
|  | 4 | 6 | 8 | 10 | 10 | 10 | 11 | 10 | 11 | 10 | 10 | 10 | 10 | 11 | 10 | 11 | CLOSE | CLOSE |  | **152** | **243.2** |
|  | 4 | 6 | 8 | 10 | 10 | 10 | 11 | 10 | 11 | 10 | 11 | 10 | 10 | 11 | 10 | 11 | CLOSE | CLOSE |  | **153** | **244.8** |
|  | 4 | 6 | 8 | 10 | 11 | 10 | 11 | 10 | 11 | 10 | 11 | 10 | 10 | 11 | 10 | 11 | CLOSE | CLOSE |  | **154** | **246.4** |
|  | 4 | 6 | 8 | 10 | 11 | 10 | 11 | 10 | 11 | 10 | 11 | 10 | 10 | 11 | 11 | 11 | CLOSE | CLOSE |  | **155** | **248.0** |
|  | 4 | 6 | 8 | 10 | 11 | 11 | 11 | 10 | 11 | 10 | 11 | 10 | 10 | 11 | 11 | 11 | CLOSE | CLOSE |  | **156** | **249.6** |
|  | 4 | 6 | 8 | 10 | 11 | 11 | 11 | 10 | 11 | 10 | 11 | 10 | 11 | 11 | 11 | 11 | CLOSE | CLOSE |  | **157** | **251.2** |
|  | 4 | 6 | 8 | 10 | 11 | 11 | 11 | 11 | 11 | 10 | 11 | 10 | 11 | 11 | 11 | 11 | CLOSE | CLOSE |  | **158** | **252.8** |
|  | 4 | 6 | 8 | 10 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 10 | 11 | 11 | 11 | 11 | CLOSE | CLOSE |  | **159** | **254.4** |
|  | 4 | 6 | 8 | 10 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | CLOSE | CLOSE |  | **160** | **256.0** |
|  | 4 | 6 | 8 | 10 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 12 | 11 | 11 | CLOSE | CLOSE |  | **161** | **257.6** |
|  | 4 | 6 | 8 | 10 | 11 | 11 | 12 | 11 | 11 | 11 | 11 | 11 | 11 | 12 | 11 | 11 | CLOSE | CLOSE |  | **162** | **259.2** |
|  | 4 | 6 | 8 | 10 | 11 | 11 | 12 | 11 | 12 | 11 | 11 | 11 | 11 | 12 | 11 | 11 | CLOSE | CLOSE |  | **163** | **260.8** |
|  | 4 | 6 | 8 | 10 | 11 | 11 | 12 | 11 | 12 | 11 | 12 | 11 | 11 | 12 | 11 | 11 | CLOSE | CLOSE |  | **164** | **262.4** |
|  | 4 | 6 | 8 | 10 | 12 | 11 | 12 | 11 | 12 | 11 | 12 | 11 | 11 | 12 | 11 | 11 | CLOSE | CLOSE |  | **165** | **264.0** |
|  | 4 | 6 | 8 | 10 | 12 | 11 | 12 | 11 | 12 | 11 | 12 | 11 | 11 | 12 | 12 | 11 | CLOSE | CLOSE |  | **166** | **265.6** |
|  | 4 | 6 | 8 | 10 | 12 | 12 | 12 | 11 | 12 | 11 | 12 | 11 | 11 | 12 | 12 | 11 | CLOSE | CLOSE |  | **167** | **267.2** |
|  | 4 | 6 | 8 | 10 | 12 | 12 | 12 | 11 | 12 | 11 | 12 | 11 | 12 | 12 | 12 | 11 | CLOSE | CLOSE |  | **168** | **268.8** |
|  | 4 | 6 | 8 | 10 | 12 | 12 | 12 | 12 | 12 | 11 | 12 | 11 | 12 | 12 | 12 | 11 | CLOSE | CLOSE |  | **169** | **270.4** |
|  | 4 | 6 | 8 | 10 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 11 | 12 | 12 | 12 | 11 | CLOSE | CLOSE |  | **170** | **272.0** |
|  | 4 | 6 | 8 | 10 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 11 | CLOSE | CLOSE |  | **171** | **273.6** |
|  | 4 | 6 | 8 | 10 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 13 | 12 | 11 | CLOSE | CLOSE |  | **172** | **275.2** |
|  | 4 | 6 | 8 | 10 | 12 | 12 | 13 | 12 | 12 | 12 | 12 | 12 | 12 | 13 | 12 | 11 | CLOSE | CLOSE |  | **173** | **276.8** |
|  | 4 | 6 | 8 | 10 | 12 | 12 | 13 | 12 | 13 | 12 | 12 | 12 | 12 | 13 | 12 | 11 | CLOSE | CLOSE |  | **174** | **278.4** |
|  | 4 | 6 | 8 | 10 | 12 | 12 | 13 | 12 | 13 | 12 | 13 | 12 | 12 | 13 | 12 | 11 | CLOSE | CLOSE |  | **175** | **280.0** |
|  | 4 | 6 | 8 | 10 | 12 | 12 | 13 | 12 | 13 | 12 | 13 | 12 | 12 | 13 | 13 | 11 | CLOSE | CLOSE |  | **176** | **281.6** |
|  | 4 | 6 | 8 | 10 | 12 | 13 | 13 | 12 | 13 | 12 | 13 | 12 | 12 | 13 | 13 | 11 | CLOSE | CLOSE |  | **177** | **283.2** |
|  | 4 | 6 | 8 | 10 | 12 | 13 | 13 | 12 | 13 | 12 | 13 | 12 | 13 | 13 | 13 | 11 | CLOSE | CLOSE |  | **178** | **284.8** |
|  | 4 | 6 | 8 | 10 | 12 | 13 | 13 | 13 | 13 | 12 | 13 | 12 | 13 | 13 | 13 | 11 | CLOSE | CLOSE |  | **179** | **286.4** |
|  | 4 | 6 | 8 | 10 | 12 | 13 | 13 | 13 | 13 | 13 | 13 | 12 | 13 | 13 | 13 | 11 | CLOSE | CLOSE |  | **180** | **288.0** |
|  | 4 | 6 | 8 | 10 | 12 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 11 | CLOSE | CLOSE |  | **181** | **289.6** |
|  | 4 | 6 | 8 | 10 | 12 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 14 | 13 | 11 | CLOSE | CLOSE |  | **182** | **291.2** |
|  | 4 | 6 | 8 | 10 | 12 | 13 | 14 | 13 | 13 | 13 | 13 | 13 | 13 | 14 | 13 | 11 | CLOSE | CLOSE |  | **183** | **292.8** |
|  | 4 | 6 | 8 | 10 | 12 | 13 | 14 | 13 | 14 | 13 | 13 | 13 | 13 | 14 | 13 | 11 | CLOSE | CLOSE |  | **184** | **294.4** |
|  | 4 | 6 | 8 | 10 | 12 | 13 | 14 | 13 | 14 | 13 | 14 | 13 | 13 | 14 | 13 | 11 | CLOSE | CLOSE |  | **185** | **296.0** |
|  | 4 | 6 | 8 | 10 | 12 | 13 | 14 | 13 | 14 | 13 | 14 | 13 | 13 | 14 | 14 | 11 | CLOSE | CLOSE |  | **186** | **297.6** |
|  | 4 | 6 | 8 | 10 | 12 | 14 | 14 | 13 | 14 | 13 | 14 | 13 | 13 | 14 | 14 | 11 | CLOSE | CLOSE |  | **187** | **299.2** |
|  | 4 | 6 | 8 | 10 | 12 | 14 | 14 | 13 | 14 | 13 | 14 | 13 | 14 | 14 | 14 | 11 | CLOSE | CLOSE |  | **188** | **300.8** |
|  | 4 | 6 | 8 | 10 | 12 | 14 | 14 | 14 | 14 | 13 | 14 | 13 | 14 | 14 | 14 | 11 | CLOSE | CLOSE |  | **189** | **302.4** |
|  | 4 | 6 | 8 | 10 | 12 | 14 | 14 | 14 | 14 | 14 | 14 | 13 | 14 | 14 | 14 | 11 | CLOSE | CLOSE |  | **190** | **304.0** |
|  | 4 | 6 | 8 | 10 | 12 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 11 | CLOSE | CLOSE |  | **191** | **305.6** |
|  | 4 | 6 | 8 | 10 | 12 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 15 | 14 | 11 | CLOSE | CLOSE |  | **192** | **307.2** |
|  | 4 | 6 | 8 | 10 | 12 | 14 | 15 | 14 | 14 | 14 | 14 | 14 | 14 | 15 | 14 | 11 | CLOSE | CLOSE |  | **193** | **308.8** |
|  | 4 | 6 | 8 | 10 | 12 | 14 | 15 | 14 | 15 | 14 | 14 | 14 | 14 | 15 | 14 | 11 | CLOSE | CLOSE |  | **194** | **310.4** |
|  | 4 | 6 | 8 | 10 | 12 | 14 | 15 | 14 | 15 | 14 | 15 | 14 | 14 | 15 | 14 | 11 | CLOSE | CLOSE |  | **195** | **312.0** |
|  | 4 | 6 | 8 | 10 | 12 | 14 | 15 | 14 | 15 | 14 | 15 | 14 | 14 | 15 | 15 | 11 | CLOSE | CLOSE |  | **196** | **313.6** |
|  | 4 | 6 | 8 | 10 | 12 | 14 | 15 | 14 | 15 | 14 | 15 | 14 | 15 | 15 | 15 | 11 | CLOSE | CLOSE |  | **197** | **315.2** |
|  | 4 | 6 | 8 | 10 | 12 | 14 | 15 | 15 | 15 | 14 | 15 | 14 | 15 | 15 | 15 | 11 | CLOSE | CLOSE |  | **198** | **316.8** |
|  | 4 | 6 | 8 | 10 | 12 | 14 | 15 | 15 | 15 | 15 | 15 | 14 | 15 | 15 | 15 | 11 | CLOSE | CLOSE |  | **199** | **318.4** |
|  | 4 | 6 | 8 | 10 | 12 | 14 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 11 | CLOSE | CLOSE |  | **200** | **320.0** |
|  | 4 | 6 | 8 | 10 | 12 | 14 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 16 | 15 | 11 | CLOSE | CLOSE |  | **201** | **321.6** |
|  | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 15 | 15 | 15 | 15 | 15 | 15 | 16 | 15 | 11 | CLOSE | CLOSE |  | **202** | **323.2** |
|  | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 15 | 16 | 15 | 15 | 15 | 15 | 16 | 15 | 11 | CLOSE | CLOSE |  | **203** | **324.8** |
|  | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 15 | 16 | 15 | 16 | 15 | 15 | 16 | 15 | 11 | CLOSE | CLOSE |  | **204** | **326.4** |
|  | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 15 | 16 | 15 | 16 | 15 | 15 | 16 | 16 | 11 | CLOSE | CLOSE |  | **205** | **328.0** |
|  | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 15 | 16 | 15 | 16 | 15 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **206** | **329.6** |
|  | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 16 | 16 | 15 | 16 | 15 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **207** | **331.2** |
|  | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 16 | 16 | 16 | 16 | 15 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **208** | **332.8** |
|  | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **209** | **334.4** |
|  | 4 | 6 | 8 | 10 | 12 | 15 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **210** | **336.0** |
|  | 4 | 6 | 8 | 10 | 13 | 15 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **211** | **337.6** |
|  | 4 | 6 | 8 | 11 | 13 | 15 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **212** | **339.2** |
|  | 4 | 6 | 9 | 11 | 13 | 15 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **213** | **340.8** |
|  | 4 | 7 | 9 | 11 | 13 | 15 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **214** | **342.4** |
|  | 5 | 7 | 9 | 11 | 13 | 15 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **215** | **344.0** |
| 1 | 5 | 7 | 9 | 11 | 13 | 15 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **216** | **345.6** |
| 1 | 5 | 7 | 9 | 11 | 13 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **217** | **347.2** |
| 1 | 5 | 7 | 9 | 11 | 14 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **218** | **348.8** |
| 1 | 5 | 7 | 9 | 12 | 14 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **219** | **350.4** |
| 1 | 5 | 7 | 10 | 12 | 14 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **220** | **352.0** |
| 1 | 5 | 8 | 10 | 12 | 14 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **221** | **353.6** |
| 1 | 6 | 8 | 10 | 12 | 14 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **222** | **355.2** |
| 2 | 6 | 8 | 10 | 12 | 14 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **223** | **356.8** |
| 2 | 6 | 8 | 10 | 12 | 15 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **224** | **358.4** |
| 2 | 6 | 8 | 10 | 13 | 15 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **225** | **360.0** |
| 2 | 6 | 8 | 11 | 13 | 15 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **226** | **361.6** |
| 2 | 6 | 9 | 11 | 13 | 15 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **227** | **363.2** |
| 2 | 7 | 9 | 11 | 13 | 15 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **228** | **364.8** |
| 3 | 7 | 9 | 11 | 13 | 15 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **229** | **366.4** |
| 3 | 7 | 9 | 11 | 13 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **230** | **368.0** |
| 3 | 7 | 9 | 11 | 14 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **231** | **369.6** |
| 3 | 7 | 9 | 12 | 14 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **232** | **371.2** |
| 3 | 7 | 10 | 12 | 14 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **233** | **372.8** |
| 3 | 8 | 10 | 12 | 14 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **234** | **374.4** |
| 4 | 8 | 10 | 12 | 14 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **235** | **376.0** |
| 4 | 8 | 10 | 12 | 15 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **236** | **377.6** |
| 4 | 8 | 10 | 13 | 15 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **237** | **379.2** |
| 4 | 8 | 11 | 13 | 15 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **238** | **380.8** |
| 4 | 9 | 11 | 13 | 15 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **239** | **382.4** |
| 5 | 9 | 11 | 13 | 15 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **240** | **384.0** |
| 5 | 9 | 11 | 13 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **241** | **385.6** |
| 5 | 9 | 11 | 14 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **242** | **387.2** |
| 5 | 9 | 12 | 14 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **243** | **388.8** |
| 5 | 10 | 12 | 14 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **244** | **390.4** |
| 6 | 10 | 12 | 14 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **245** | **392.0** |
| 6 | 10 | 12 | 15 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **246** | **393.6** |
| 6 | 10 | 13 | 15 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **247** | **395.2** |
| 6 | 11 | 13 | 15 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **248** | **396.8** |
| 7 | 11 | 13 | 15 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **249** | **398.4** |
| 7 | 11 | 13 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **250** | **400.0** |
| 7 | 11 | 14 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **251** | **401.6** |
| 8 | 11 | 14 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **252** | **403.2** |
| 8 | 11 | 15 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **253** | **404.8** |
| 9 | 11 | 15 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **254** | **406.4** |
| 9 | 11 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **255** | **408.0** |
| 10 | 11 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **256** | **409.6** |
| 11 | 11 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **257** | **411.2** |
| 11 | 11 | 17 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **258** | **412.8** |
| 11 | 11 | 17 | 17 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | CLOSE | CLOSE |  | **259** | **414.4** |
| 11 | 11 | 17 | 17 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 17 | 16 | 11 | CLOSE | CLOSE |  | **260** | **416.0** |
| 11 | 11 | 17 | 17 | 17 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 17 | 16 | 11 | CLOSE | CLOSE |  | **261** | **417.6** |
| 11 | 11 | 17 | 17 | 17 | 16 | 16 | 17 | 16 | 16 | 16 | 16 | 16 | 16 | 17 | 16 | 11 | CLOSE | CLOSE |  | **262** | **419.2** |
| 11 | 11 | 17 | 17 | 17 | 16 | 16 | 17 | 16 | 17 | 16 | 16 | 16 | 16 | 17 | 16 | 11 | CLOSE | CLOSE |  | **263** | **420.8** |
| 11 | 11 | 17 | 17 | 17 | 16 | 16 | 17 | 16 | 17 | 16 | 17 | 16 | 16 | 17 | 16 | 11 | CLOSE | CLOSE |  | **264** | **422.4** |
| 11 | 11 | 17 | 17 | 17 | 17 | 16 | 17 | 16 | 17 | 16 | 17 | 16 | 16 | 17 | 16 | 11 | CLOSE | CLOSE |  | **265** | **424.0** |
| 11 | 11 | 17 | 17 | 17 | 17 | 16 | 17 | 16 | 17 | 16 | 17 | 16 | 16 | 17 | 17 | 11 | CLOSE | CLOSE |  | **266** | **425.6** |
| 11 | 11 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 17 | 16 | 17 | 16 | 16 | 17 | 17 | 11 | CLOSE | CLOSE |  | **267** | **427.2** |
| 11 | 11 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 17 | 16 | 17 | 16 | 17 | 17 | 17 | 11 | CLOSE | CLOSE |  | **268** | **428.8** |
| 11 | 11 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 17 | 16 | 17 | 17 | 17 | 11 | CLOSE | CLOSE |  | **269** | **430.4** |
| 11 | 11 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 17 | 17 | 17 | 11 | CLOSE | CLOSE |  | **270** | **432.0** |
| 11 | 11 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 11 | CLOSE | CLOSE |  | **271** | **433.6** |
| 11 | 11 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 11 | CLOSE | CLOSE |  | **272** | **435.2** |
| 11 | 11 | 18 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 11 | CLOSE | CLOSE |  | **273** | **436.8** |
| 11 | 11 | 18 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 17 | 11 | CLOSE | CLOSE |  | **274** | **438.4** |
| 11 | 11 | 18 | 18 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 17 | 11 | CLOSE | CLOSE |  | **275** | **440.0** |
| 11 | 11 | 18 | 18 | 18 | 17 | 17 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 17 | 11 | CLOSE | CLOSE |  | **276** | **441.6** |
| 11 | 11 | 18 | 18 | 18 | 17 | 17 | 18 | 17 | 18 | 17 | 17 | 17 | 17 | 18 | 17 | 11 | CLOSE | CLOSE |  | **277** | **443.2** |
| 11 | 11 | 18 | 18 | 18 | 17 | 17 | 18 | 17 | 18 | 17 | 18 | 17 | 17 | 18 | 17 | 11 | CLOSE | CLOSE |  | **278** | **444.8** |
| 11 | 11 | 18 | 18 | 18 | 18 | 17 | 18 | 17 | 18 | 17 | 18 | 17 | 17 | 18 | 17 | 11 | CLOSE | CLOSE |  | **279** | **446.4** |
| 11 | 11 | 18 | 18 | 18 | 18 | 17 | 18 | 17 | 18 | 17 | 18 | 17 | 17 | 18 | 18 | 11 | CLOSE | CLOSE |  | **280** | **448.0** |
| 11 | 11 | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 18 | 17 | 18 | 17 | 17 | 18 | 18 | 11 | CLOSE | CLOSE |  | **281** | **449.6** |
| 11 | 11 | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 18 | 17 | 18 | 17 | 18 | 18 | 18 | 11 | CLOSE | CLOSE |  | **282** | **451.2** |
| 11 | 11 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 18 | 17 | 18 | 18 | 18 | 11 | CLOSE | CLOSE |  | **283** | **452.8** |
| 11 | 11 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 18 | 18 | 18 | 11 | CLOSE | CLOSE |  | **284** | **454.4** |
| 11 | 11 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 11 | CLOSE | CLOSE |  | **285** | **456.0** |
| 11 | 11 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 11 | CLOSE | CLOSE |  | **286** | **457.6** |
| 11 | 11 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 11 | CLOSE | CLOSE |  | **287** | **459.2** |
| 11 | 11 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 18 | 11 | CLOSE | CLOSE |  | **288** | **460.8** |
| 11 | 11 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 18 | 11 | CLOSE | CLOSE |  | **289** | **462.4** |
| 11 | 11 | 19 | 19 | 19 | 18 | 18 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 18 | 11 | CLOSE | CLOSE |  | **290** | **464.0** |
| 11 | 11 | 19 | 19 | 19 | 18 | 18 | 19 | 18 | 19 | 18 | 18 | 18 | 18 | 19 | 18 | 11 | CLOSE | CLOSE |  | **291** | **465.6** |
| 11 | 11 | 19 | 19 | 19 | 18 | 18 | 19 | 18 | 19 | 18 | 19 | 18 | 18 | 19 | 18 | 11 | CLOSE | CLOSE |  | **292** | **467.2** |
| 11 | 11 | 19 | 19 | 19 | 19 | 18 | 19 | 18 | 19 | 18 | 19 | 18 | 18 | 19 | 18 | 11 | CLOSE | CLOSE |  | **293** | **468.8** |
| 11 | 11 | 19 | 19 | 19 | 19 | 18 | 19 | 18 | 19 | 18 | 19 | 18 | 18 | 19 | 19 | 11 | CLOSE | CLOSE |  | **294** | **470.4** |
| 11 | 11 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 19 | 18 | 19 | 18 | 18 | 19 | 19 | 11 | CLOSE | CLOSE |  | **295** | **472.0** |
| 11 | 11 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 19 | 18 | 19 | 18 | 19 | 19 | 19 | 11 | CLOSE | CLOSE |  | **296** | **473.6** |
| 11 | 11 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 19 | 18 | 19 | 19 | 19 | 11 | CLOSE | CLOSE |  | **297** | **475.2** |
| 11 | 11 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 19 | 19 | 19 | 11 | CLOSE | CLOSE |  | **298** | **476.8** |
| 11 | 11 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 11 | CLOSE | CLOSE |  | **299** | **478.4** |
| 11 | 11 | 20 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 11 | CLOSE | CLOSE |  | **300** | **480.0** |
| 11 | 11 | 20 | 20 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 11 | CLOSE | CLOSE |  | **301** | **481.6** |
| 11 | 11 | 20 | 20 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 19 | 11 | CLOSE | CLOSE |  | **302** | **483.2** |
| 11 | 11 | 20 | 20 | 20 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 19 | 11 | CLOSE | CLOSE |  | **303** | **484.8** |
| 11 | 11 | 20 | 20 | 20 | 19 | 19 | 20 | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 19 | 11 | CLOSE | CLOSE |  | **304** | **486.4** |
| 11 | 11 | 20 | 20 | 20 | 19 | 19 | 20 | 19 | 20 | 19 | 19 | 19 | 19 | 20 | 19 | 11 | CLOSE | CLOSE |  | **305** | **488.0** |
| 11 | 11 | 20 | 20 | 20 | 19 | 19 | 20 | 19 | 20 | 19 | 20 | 19 | 19 | 20 | 19 | 11 | CLOSE | CLOSE |  | **306** | **489.6** |
| 11 | 11 | 20 | 20 | 20 | 20 | 19 | 20 | 19 | 20 | 19 | 20 | 19 | 19 | 20 | 19 | 11 | CLOSE | CLOSE |  | **307** | **491.2** |
| 11 | 11 | 20 | 20 | 20 | 20 | 19 | 20 | 19 | 20 | 19 | 20 | 19 | 19 | 20 | 20 | 11 | CLOSE | CLOSE |  | **308** | **492.8** |
| 11 | 11 | 20 | 20 | 20 | 20 | 20 | 20 | 19 | 20 | 19 | 20 | 19 | 19 | 20 | 20 | 11 | CLOSE | CLOSE |  | **309** | **494.4** |
| 11 | 11 | 20 | 20 | 20 | 20 | 20 | 20 | 19 | 20 | 19 | 20 | 19 | 20 | 20 | 20 | 11 | CLOSE | CLOSE |  | **310** | **496.0** |
| 11 | 11 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 19 | 20 | 19 | 20 | 20 | 20 | 11 | CLOSE | CLOSE |  | **311** | **497.6** |
| 11 | 11 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 19 | 20 | 20 | 20 | 11 | CLOSE | CLOSE |  | **312** | **499.2** |
| 11 | 11 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 11 | CLOSE | CLOSE |  | **313** | **500.8** |
| 11 | 11 | 21 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 11 | CLOSE | CLOSE |  | **314** | **502.4** |
| 11 | 11 | 21 | 21 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 11 | CLOSE | CLOSE |  | **315** | **504.0** |
| 11 | 11 | 21 | 21 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 20 | 11 | CLOSE | CLOSE |  | **316** | **505.6** |
| 11 | 11 | 21 | 21 | 21 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 20 | 11 | CLOSE | CLOSE |  | **317** | **507.2** |
| 11 | 11 | 21 | 21 | 21 | 20 | 20 | 21 | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 20 | 11 | CLOSE | CLOSE |  | **318** | **508.8** |
| 11 | 11 | 21 | 21 | 21 | 20 | 20 | 21 | 20 | 21 | 20 | 20 | 20 | 20 | 21 | 20 | 11 | CLOSE | CLOSE |  | **319** | **510.4** |
| 11 | 11 | 21 | 21 | 21 | 20 | 20 | 21 | 20 | 21 | 20 | 21 | 20 | 20 | 21 | 20 | 11 | CLOSE | CLOSE |  | **320** | **512.0** |
| 11 | 11 | 21 | 21 | 21 | 21 | 20 | 21 | 20 | 21 | 20 | 21 | 20 | 20 | 21 | 20 | 11 | CLOSE | CLOSE |  | **321** | **513.6** |
| 11 | 11 | 21 | 21 | 21 | 21 | 20 | 21 | 20 | 21 | 20 | 21 | 20 | 20 | 21 | 21 | 11 | CLOSE | CLOSE |  | **322** | **515.2** |
| 11 | 11 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 21 | 20 | 21 | 20 | 20 | 21 | 21 | 11 | CLOSE | CLOSE |  | **323** | **516.8** |
| 11 | 11 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 21 | 20 | 21 | 20 | 21 | 21 | 21 | 11 | CLOSE | CLOSE |  | **324** | **518.4** |
| 11 | 11 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 21 | 20 | 21 | 21 | 21 | 11 | CLOSE | CLOSE |  | **325** | **520.0** |
| 11 | 11 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 21 | 21 | 21 | 11 | CLOSE | CLOSE |  | **326** | **521.6** |
| 11 | 11 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 11 | CLOSE | CLOSE |  | **327** | **523.2** |
| 11 | 11 | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 11 | CLOSE | CLOSE |  | **328** | **524.8** |
| 11 | 11 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 11 | CLOSE | CLOSE |  | **329** | **526.4** |
| 11 | 11 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 22 | 21 | 11 | CLOSE | CLOSE |  | **330** | **528.0** |
| 11 | 11 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 22 | 21 | 11 | CLOSE | CLOSE |  | **331** | **529.6** |
| 11 | 11 | 22 | 22 | 22 | 21 | 21 | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 22 | 21 | 11 | CLOSE | CLOSE |  | **332** | **531.2** |
| 11 | 11 | 22 | 22 | 22 | 21 | 21 | 22 | 21 | 22 | 21 | 21 | 21 | 21 | 22 | 21 | 11 | CLOSE | CLOSE |  | **333** | **532.8** |
| 11 | 11 | 22 | 22 | 22 | 21 | 21 | 22 | 21 | 22 | 21 | 22 | 21 | 21 | 22 | 21 | 11 | CLOSE | CLOSE |  | **334** | **534.4** |
| 11 | 11 | 22 | 22 | 22 | 22 | 21 | 22 | 21 | 22 | 21 | 22 | 21 | 21 | 22 | 21 | 11 | CLOSE | CLOSE |  | **335** | **536.0** |
| 11 | 11 | 22 | 22 | 22 | 22 | 21 | 22 | 21 | 22 | 21 | 22 | 21 | 21 | 22 | 22 | 11 | CLOSE | CLOSE |  | **336** | **537.6** |
| 11 | 11 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 22 | 21 | 22 | 21 | 21 | 22 | 22 | 11 | CLOSE | CLOSE |  | **337** | **539.2** |
| 11 | 11 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 22 | 21 | 22 | 21 | 22 | 22 | 22 | 11 | CLOSE | CLOSE |  | **338** | **540.8** |
| 11 | 11 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 22 | 21 | 22 | 22 | 22 | 11 | CLOSE | CLOSE |  | **339** | **542.4** |
| 11 | 11 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 22 | 22 | 22 | 11 | CLOSE | CLOSE |  | **340** | **544.0** |
| 11 | 11 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 11 | CLOSE | CLOSE |  | **341** | **545.6** |
| 11 | 11 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 11 | CLOSE | CLOSE |  | **342** | **547.2** |
| 11 | 11 | 23 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 11 | CLOSE | CLOSE |  | **343** | **548.8** |
| 11 | 11 | 23 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 23 | 22 | 11 | CLOSE | CLOSE |  | **344** | **550.4** |
| 11 | 11 | 23 | 23 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 23 | 22 | 11 | CLOSE | CLOSE |  | **345** | **552.0** |
| 11 | 11 | 23 | 23 | 23 | 22 | 22 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | 23 | 22 | 11 | CLOSE | CLOSE |  | **346** | **553.6** |
| 11 | 11 | 23 | 23 | 23 | 22 | 22 | 23 | 22 | 23 | 22 | 22 | 22 | 22 | 23 | 22 | 11 | CLOSE | CLOSE |  | **347** | **555.2** |
| 11 | 11 | 23 | 23 | 23 | 22 | 22 | 23 | 22 | 23 | 22 | 23 | 22 | 22 | 23 | 22 | 11 | CLOSE | CLOSE |  | **348** | **556.8** |
| 11 | 11 | 23 | 23 | 23 | 23 | 22 | 23 | 22 | 23 | 22 | 23 | 22 | 22 | 23 | 22 | 11 | CLOSE | CLOSE |  | **349** | **558.4** |
| 11 | 11 | 23 | 23 | 23 | 23 | 22 | 23 | 22 | 23 | 22 | 23 | 22 | 22 | 23 | 23 | 11 | CLOSE | CLOSE |  | **350** | **560.0** |
| 11 | 11 | 23 | 23 | 23 | 23 | 23 | 23 | 22 | 23 | 22 | 23 | 22 | 22 | 23 | 23 | 11 | CLOSE | CLOSE |  | **351** | **561.6** |
| 11 | 11 | 23 | 23 | 23 | 23 | 23 | 23 | 22 | 23 | 22 | 23 | 22 | 23 | 23 | 23 | 11 | CLOSE | CLOSE |  | **352** | **563.2** |
| 11 | 11 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 22 | 23 | 22 | 23 | 23 | 23 | 11 | CLOSE | CLOSE |  | **353** | **564.8** |
| 11 | 11 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 22 | 23 | 23 | 23 | 11 | CLOSE | CLOSE |  | **354** | **566.4** |
| 11 | 11 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 11 | CLOSE | CLOSE |  | **355** | **568.0** |
| 11 | 11 | 24 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 11 | CLOSE | CLOSE |  | **356** | **569.6** |
| 11 | 11 | 24 | 24 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 11 | CLOSE | CLOSE |  | **357** | **571.2** |
| 11 | 11 | 24 | 24 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 24 | 23 | 11 | CLOSE | CLOSE |  | **358** | **572.8** |
| 11 | 11 | 24 | 24 | 24 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 24 | 23 | 11 | CLOSE | CLOSE |  | **359** | **574.4** |
| 11 | 11 | 24 | 24 | 24 | 23 | 23 | 24 | 23 | 23 | 23 | 23 | 23 | 23 | 24 | 23 | 11 | CLOSE | CLOSE |  | **360** | **576.0** |
| 11 | 11 | 24 | 24 | 24 | 23 | 23 | 24 | 23 | 24 | 23 | 23 | 23 | 23 | 24 | 23 | 11 | CLOSE | CLOSE |  | **361** | **577.6** |
| 11 | 11 | 24 | 24 | 24 | 23 | 23 | 24 | 23 | 24 | 23 | 24 | 23 | 23 | 24 | 23 | 11 | CLOSE | CLOSE |  | **362** | **579.2** |
| 11 | 11 | 24 | 24 | 24 | 24 | 23 | 24 | 23 | 24 | 23 | 24 | 23 | 23 | 24 | 23 | 11 | CLOSE | CLOSE |  | **363** | **580.8** |
| 11 | 11 | 24 | 24 | 24 | 24 | 23 | 24 | 23 | 24 | 23 | 24 | 23 | 23 | 24 | 24 | 11 | CLOSE | CLOSE |  | **364** | **582.4** |
| 11 | 11 | 24 | 24 | 24 | 24 | 24 | 24 | 23 | 24 | 23 | 24 | 23 | 23 | 24 | 24 | 11 | CLOSE | CLOSE |  | **365** | **584.0** |
| 11 | 11 | 24 | 24 | 24 | 24 | 24 | 24 | 23 | 24 | 23 | 24 | 23 | 24 | 24 | 24 | 11 | CLOSE | CLOSE |  | **366** | **585.6** |
| 11 | 11 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 23 | 24 | 23 | 24 | 24 | 24 | 11 | CLOSE | CLOSE |  | **367** | **587.2** |
| 11 | 11 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 23 | 24 | 24 | 24 | 11 | CLOSE | CLOSE |  | **368** | **588.8** |
| 11 | 11 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 11 | CLOSE | CLOSE |  | **369** | **590.4** |
| 11 | 11 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 11 | CLOSE | CLOSE |  | **370** | **592.0** |
| 11 | 11 | 25 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 11 | CLOSE | CLOSE |  | **371** | **593.6** |
| 11 | 11 | 25 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 25 | 24 | 11 | CLOSE | CLOSE |  | **372** | **595.2** |
| 11 | 11 | 25 | 25 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 25 | 24 | 11 | CLOSE | CLOSE |  | **373** | **596.8** |
| 11 | 11 | 25 | 25 | 25 | 24 | 24 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 25 | 24 | 11 | CLOSE | CLOSE |  | **374** | **598.4** |
| 11 | 11 | 25 | 25 | 25 | 24 | 24 | 25 | 24 | 25 | 24 | 24 | 24 | 24 | 25 | 24 | 11 | CLOSE | CLOSE |  | **375** | **600.0** |

1. Data are for powerhouse passage only. Recent radio-tracking and hydroacoustic data indicate different passage patterns for the spillway and project when spill is occurring 24 hours/day. [↑](#footnote-ref-1)
2. Daily adult salmon counts: <https://www.fpc.org/currentdaily/HistFishTwo_7day-ytd_Adults.htm> [↑](#footnote-ref-2)
3. TDG Management Plan (Appendix 4 of the WMP) - [pweb.crohms.org/tmt/documents/wmp/](http://pweb.crohms.org/tmt/documents/wmp/)

   TDG Monitoring Plan of Action - [www.nwd.usace.army.mil/Missions/Water/Columbia/Water-Quality](https://www.nwd.usace.army.mil/Missions/Water/Columbia/Water-Quality)/ [↑](#footnote-ref-3)
4. FPC ladder temperature data website: [www.fpc.org/smolt/smolt\_queries/Q\_ladderwatertempgraphv2.php](https://www.fpc.org/smolt/smolt_queries/Q_ladderwatertempgraphv2.php) [↑](#footnote-ref-4)
5. Dewatering Plans are available on the FPOM website at: [pweb.crohms.org/tmt/documents/FPOM/2010/](http://pweb.crohms.org/tmt/documents/FPOM/2010/) [↑](#footnote-ref-5)
6. Head gates may also be referred to as “operating” gates at some projects. The terms are interchangeable. [↑](#footnote-ref-6)
7. Spill (kcfs) is calculated as a function of total stops + TSW spill. At Spill > 305 kcfs, transition from pattern for juvenile fish to flood. [↑](#footnote-ref-7)
8. Gates 1 & 20 blocked at 11 stops (10.3 ft opening). [↑](#footnote-ref-8)
9. TSWs in Bays 18-19 = fixed spill of ~19.4 kcfs (~9.7 kcfs/bay). TSW removal recommended for flow > 685 kcfs. TSW does not affect spillway flood capacity until flow ≥ 1,492 kcfs. [↑](#footnote-ref-9)
10. Spill (kcfs) is calculated as a function of total stops + TSW spill. At Spill >305 kcfs, transition from pattern for juvenile fish to flood. [↑](#footnote-ref-10)
11. Gates 1 & 20 blocked at 11 stops (10.3 ft opening). [↑](#footnote-ref-11)